## USER GUIDE - SO (hidden)
EDM Storm Overflow Annual Return: Quick User Guide
!! See separate User Guide in Word format for further detail !!
General Guidance:
- The EDM annual return 2021 should list all storm overflows with spills to the environment (permitted/unpermitted with permit application made), irrespective of whether they are currently have EDM installed or existing EDM permit condition.
- The EDM annual return 2021 should include data for (1) All storm overflows with an existing EDM permit condition, and (2) All storm overflows with EDM intalled through the WINEP/AMP7 EDM programme, with or without a current EDM permit condition. Data should also be included for overflows where a permit has been applied for by the WaSC but not yet issued.
- WaSCs are expected to provide EDM data for overflows without a current EDM requirement (e.g. not secured through the WINEP nor with a permit requirement), where they deem this data accurate & representative of spills
- Reported spill data (count & duration) should be considered reliable, verified and an accurate representation of the spills that occurred during the reporting period. Data that is known to be erroneous should not be reported on. See main User Guide (Word document) for more information and examples.
- Base information (e.g. EA permit reference, site name, Outlet NGR etc.) on overflows must directly match the Environment Agency (EA) Consents Database (see "Resources" below).
- Where EDM reporting operability is <90% (Column Q) subsequent columns Primary Reason (Column R) and Action Taken / Planned (Column S) must be completed.
- If spill count data (column P + valid data in previous years) exceeds thresholds in the SOAF guidance then columns T, U, V (Spill Frequency - operational & planning info) must be completed.
- A number of columns are "do once"; the data are not expected to change year on year. These headings are highlighted in grey below. Data in remaining columns are expected to change each year. These headings are highlighted in light green below.
- Water Framework Directive (WFD) data in columns I & J have been pre-populated by the EA using the Outlet NGR provided by WaSCs [November 2021] in column H.
- Any additional overflows not previously provided, or newly-reconciled Consents Database permit references must be submitted by WaSCs to the EA by Friday 21 January 2022. The EA will then identify the relevant WFD information & return to WaSCs on Friday 28 January ahead of final submission by WaSCs the following month.
Resources:
- Environment Agency national consents database: |  | Consented Discharges to Controlled Waters with Conditions - data.gov.uk
(Note the EA Consents Database is updated quarterly on .gov.uk)
- Environment Agency Risk-Based Approach to the Monitoring of Storm Discharges (September 2013)
- Environment Agency Storm Overflow Assessment Framework (June 2018): |  |  | Storm Overflow Assessment Framework
Guide to columns & drop-down selection:
Water Company Name | (Column A)
Site Name (EA Consents Database) | (Column B)
- Site name that matches exactly with column "Discharge_Site_Name" on EA consents database
Site Name (WaSC Operational Name) | (Column C)
- Site name used by the WaSC for operational reasons. The EA Consents Database Site Name must be provided in column B - the WaSC site name is not a substitute
- Column C is optional
EA Consents Database Permit Reference | (Column D)
- As shown in column "Permit Number" on EA Consents Database. NB: this may occassionally differ from number shown on actual permit or WaSC URN/folio
WaSC Supplementary Permit Ref. | (Column E)
- WaSC reference number for permitted overflow. The EA Consents Database permit reference must be provided in column D - the WaSC permit reference is not a substitute
- Column E is optional
Activity reference | (Column F)
- Listed on new format permits under Schedule 1 – “Operations” (e.g. A1 / A2 etc.)
- Listed on old format permits under Schedule conditions (e.g. Schedule No. A.115K/00-01)
- NB: This is not the same as columns “DISCHARGE_SITE_TYPE_CODE” or “DSI_TYPE_DESCRIPTION” on EA consents database
Storm discharge asset type | (Column G)
- As detailed in risk-based approach to EDM document (2013)
- See the more detailed User Guide (Word format) for a table of definitions (page 6)
- NB: This is not the same as columns “DISCHARGE_SITE_TYPE_CODE” or “DSI_TYPE_DESCRIPTION” on EA consents database
Drop-down options Column G:
SO on sewer network | On network - storm overflow. Can be direct or associated with a network storm tank. Not associated with pumping station
Storm discharge at pumping station | On network - pumping station
Inlet SO at WwTW | Storm overflow (direct to the environment) permitted as part of a WwTW permit. Exception is a storm tank - see note on next row
Storm tank at WwTW | Storm overflow via a storm tank, permitted as part of a WwTW permit. Note this can be physically remote from the WwTW
Other storm discharge asset type | Any storm overflow that does not clearly align with the four categories above. These may be used to devlop future drop-down categories.
Outlet discharge NGR (Consents Database) | (Column H)
- This is the actual discharge point to the environment.
- Listed on EA consents database as “OUTLET_GRID_REF”. This is the reference to use
- Also listed on new format permits under Schedule 3 - "Discharge Point NGR"
- Also listed on old format permits under "Place of Discharge"
- NB: This is not the same as columns “DISCHARGE_NGR” (discarhge site NGR) or “EFFLUENT_GRID_REF” (effluent monitoring NGR) on EA consents database
WFD Waterbody ID (Cycle 2) | (Column I)
- Identification number of WFD waterbody at the discharge point (as per Cycle 2)
- Prefixed with "GB…"
- Pre-populated by EA using outlet discharge NGR (column H). Any further overflows requiring the EA to populate WFD information must be submitted to the EA by Friday 21 January 2022
WFD Waterbody Catchment Name (Cycle 2) | (Column J)
- Name of WFD waterbody catchment at the discharge point (as per Cycle 2)
- NB: This is not the same as "CATC_NAME" on EA consents database
- Pre-populated by EA using outlet discharge NGR (column H). Any further overflows requiring the EA to populate WFD information must be submitted to the EA by Friday 21 January 2022
Receiving Water / Environment - common name (Consents Database) | (Column K)
- Listed on EA consents database under "RECEIVING_WATER" NB: this may differ from receiving water shown on actual permit
- Also listed on new format permits under Schedule 3 - "Discharge Point"
- Also listed on old format permits under "Place of Discharge"
Shellfishery | (Column L)
- Populate for storm overflows that have Shellfish Water EDM requirements
Bathing Beach | (Column M)
- Populate for storm overflows that have Bathing Water EDM requirements
Initial EDM commission date | (Column N)
- Date EDM commissioned; the date data can be expected from the EDM
- See the more detailed User Guide (Word format) for more detailed table of definitions (page 7)
- Note: Installation date may precede commissioned date
Drop-down options Column M:
Installed but not yet commissioned | Installed in current reporting year but data not yet expected
Commissioned in 2020 - full year data expected | Installed in previous reporting year
Commissioned in 2019 - full year data expected | Installed in previous reporting year
Commissioned in 2018 - full year data expected | Installed in previous reporting year
Commissioned in 2017 - full year data expected | Installed in previous reporting year
Commissioned in 2016 - full year data expected | Installed in previous reporting year
Commissioned pre-2016 - full year data expected | Installed in previous reporting year
Jan 2021
Feb 2021
Mar 2021
April 2021
May 2021
June 2021
July 2021
August 2021
September 2021
October 2021
November 2021
December 2021
EDM to be installed by December 2023 | EDM not yet installed
Total Duration (hr) of all spills | (Column O)
- Total spill duration prior to processing through the 12-24h count method
Counted spills using 12-24h count method | (Column P)
- Spill count post-processed through the 12-24h count method
EDM Operation - % reporting period EDM operational | (Column Q)
- Based on Initial Commissioning Date (Column M) e.g. commissioned in July of reporting year then period Jul-Dec would be 100%; if commissioned in previous reporting year then period Jan-Dec would be 100%
- e.g. commissioned in September of reporting year then 100% reporting period would be Sep.-Dec.
- e.g. commissioned in any previous reporting year then 100% reporting period would be Jan.-Dec.
- See the more detailed User Guide (Word format) for further information & examples
EDM Operation - Reporting % - Primary Reason <90% | (Column R)
- Core reason why EDM may not have been operational <90% of period (Column Q)
- Select primary reason only
- Category must be selected when period of EDM operation (column Q) is less than 90%. Optional to complete this column when period of EDM operation is 90% or over
- See the more detailed User Guide (Word format) for table of definitions (page 8)
Drop-down options Column R:
Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | When access causes inability to retrieve data; e.g. landowner permission. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead. Not to be used for delayed access t fix existing operational fault
Capital / maintenance works affect EDM operation | Where planned works affect EDM operation. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead
Comms failure / issue | Any part of communication failure; e.g. intermittent signal or antenna damage. Consider core reason – if caused by poor installation or design then select “Installation set-up/design issue” category instead. Similar if comms loss caused by power failure – select “Power failure / issue” instead
EDM not yet installed | E.g. not yet scheduled for installation, or installation not currently feasible
EDM installed - not yet commissioned | E.g. installed after reporting period. E.g. installed within reporting period but data not yet calibrated
Installation set-up/design issue | When installation or design (e.g. choice of location) affects EDM operability. E.g. Original design location cannot distinguish between two overflows & original EDM needs to be relocated to more representative point. E.g. Original design location affected by river ingress & EDM requires relocation. E.g. Alternative monitor type required
Power failure / issue | Any part of power failure; e.g. loss of mains supply / battery fault. Consider core reason – if caused by cutting through cable then select “Capital / maintenance works” category instead
Sensor failure / issue | Any part of sensor failure; e.g. water ingress to connection between sensor & logger. Consider core reason – if water ingress caused by poor choice of location for installation & requires adjustment then select “Installation set-up/design issue” category instead
Telemetry or data archiving failure / issue | Any part of telemetry failure; e.g. dial-in or storage/sending of data problems. Consider core reason – if archiving problem caused by power fault or incorrect installation then use “Power failure / issue” or ”Installation set-up/design issue” categories respectively. Similar if data transfer caused by intermittent signal – select “Comms failure / issue” instead
No longer operational as an overflow - permit revoked or to be revoked
Reporting % - Action taken / planned - Status & Timeframe | (Column S)
- Indicate whether action has already been taken / is planned to be taken, or whether there is an ongoing investigation to identify the appropriate action
- Which month this activity was completed / is planned
- See the more detailed User Guide (Word format) for table of definitions (page 10)
Drop-down options Column R:
Scheduled | Appropriate operational action to address <90% EDM operation is planned
Resolved - January | Appropriate operational action has already been taken & issue affecting EDM operation resolved
Resolved - Feburary | As above
Resolved - March | As above
Resolved - April | As above
Resolved - May | As above
Resolved - June | As above
Resolved - July | As above
Resolved - August | As above
Resolved - September | As above
Resolved - October | As above
Resolved - November | As above
Resolved - December | As above
N/A - Ongoing investigation | Appropriate action not yet identified
N/A - EDM to be installed by December 2023 | Use when selection in Column R is “EDM not yet installed”
Spill Frequency - Operational Review Outcome - Primary Reason | (Column T)
- Core reason for spill count (Column P)
- Select primary reason only
- Category must be selected when spill frequency exceeds SOAF threshold (using column P + data from previous years)
- See the more detailed User Guide (Word format) for table of definitions (page 10)
Drop-down options Column T:
Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Spill frequency primarily caused by maintenance issue; e.g. roots causing channel restriction e.g. blocked screens causing premature spills
Performance - Sewer collapse (partial / full) - infrastructure issue | Spill frequency primarily caused by infrastructure issue; e.g. partial collapse of sewer
Performance - Groundwater inundation | Groundwater inundation is primary reason for spills; e.g. GW inundation in chalk catchment causing high spill frequency
Performance - Infiltration | High spill frequency caused by infiltration. Requires investment to infrastructure to resolve
Performance - Asset power failure | E.g. frequent power supply failure caused high spill frequency
Performance - Pump failure / issue | Spill frequency primarily caused by pump failure / premature spills; e.g. pumping station struggles to maintain PFF & review of rising main design required
Performance - Other maintenance / capital works (e.g. jetting) | Spill frequency primarily caused by works; e.g. jetting
Performance - Not designed to meet Bathing / Shellfish Water directive | Spill frequency threshold reached because asset not yet designed to meet BW or SFW requirements
Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Spill frequency primarily caused by inappropriate asset/configuration; e.g. inlet design causing premature spills & requires further investigation
Data collection - EDM non-representative location | E.g. Records multiple discharge points & cannot distinguish between the two. Requires relocation
Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | High spill frequency caused by exceptional weather events. Subsequent analysis of these data show adjusted spill frequency now not above SOAF threshold
Data collection - Tidal / river inundation | EDM spill frequency data quality affected by tidal or river inundation; e.g. tidal cycle causes levels to reverse flows in outfall pipe
Data collection - Poor quality (e.g. logger calibration / sensor issues) | E.g. logger calibration / sensor issues
Not asset maintenance - hydraulic capacity | Spill frequency primarily caused by hydraulic capacity issue rather than something that can be fixed operationally
Spill Frequency - Action taken / planned - Status & Timeframe | (Column U)
- Indicate whether action has already been taken / is planned to be taken, or whether there is an ongoing investigation to identify the appropriate action
- Which month this activity was completed / is planned
- Category must be selected when spill frequency exceeds SOAF threshold (using column P + data from previous years)
- See the more detailed User Guide (Word format) for table of definitions (page 11)
Drop-down options Column U:
Scheduled | Appropriate operational action to address spill frequency is planned
Resolved - January | Appropriate operational action has already been taken & issue affecting spill frequency resolved
Resolved - Feburary | As above
Resolved - March | As above
Resolved - April | As above
Resolved - May | As above
Resolved - June | As above
Resolved - July | As above
Resolved - August | As above
Resolved - September | As above
Resolved - October | As above
Resolved - November | As above
Resolved - December | As above
N/A - Ongoing investigation | Appropriate operational action not yet identified
N/A - Hydraulic Capacity | Issue is due to hydraulic capacity and unable to be fixed operationally through asset maintenance programme
Spill Frequency - Planning review position | (Column V)
- Action taken to address spill performance through the planning framework
- Select primary reason only
- Category must be selected when spill frequency exceeds SOAF threshold (using column O + data from previous years)
- Follows SOAF for addressing high frequency discharges from storm overflows under the UWWTR (see Figure 1 in SOAF document, 2018)
- Stage 1 of the SOAF should be applied to all high spills as good practice, as part of the initial investigation to understand whether spills were due to exceptional weather events, asset performance or hydraulic capacity. Stage 1 is expected on a continual rolling basis independent of any WINEP drivers.
- Progressing further past stage 1 is expected when a WINEP driver exists. Progressing past stage 1 without a WINEP driver would be proactive but at WaSC discretion.
- See the more detailed User Guide (Word format) for table of definitions (page 12)
Drop-down options Column V:
SOAF N/A - Proposed SFTP (overflow previously improved) | Schemes previously improved via SOAF but now identified for Spill Frequency Trigger Permitting
Stage 1a: Confirmed "exceptional weather" issue | See SOAF definition
Stage 1b: Confirmed "asset maintenance" issue | See SOAF definition
Stage 1c: Confirmed "hydraulic issue" | If not “exceptional weather” or “asset maintenance”
U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | SOAF invesitgation ongoing at Stage 2/3
U_INV driver - Stage 4: Cost beneficial outcome not yet determined | In process of Cost Benefit Analysis (CBA) but no outcome at present
U_INV driver - Stage 4: No cost beneficial solution | CBA indicates costs are disproportionate to environmental benefit
U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery | U_INV CBA indicates spill reduction scheme is cost beneficial and is on current WINEP or other planned improvement programme
U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery | U_INV CBA indicates a spill reduction scheme may be cost beneficial
N/A - Operational solution applied | Planning framework not required - spill frequency remedied through operational solution

## Storm Overflows
EDM STORM OVERFLOW REGULATORY ANNUAL RETURN | [8 empty] | Change made to original 2021 data return
Please send to email inbox: askED@environment-agency.gov.uk
Please name file using the following convention: "EDM Return WaSC period.xls" .
For example if Severn Trent Water had a bathing water return for 2021 it would be "EDM Return Severn Trent Water Bathing Season 2021.xls"
For example if Wessex Water had a storm overflow annual return for 2021 it would be "EDM Return Wessex Water Storm Overflow Annual 2021.xls"
For example if Southern Water had an emergency overflow annual return for 2021 it would be "EDM Return Southern Water Emergency Overflow Annual 2021.xls"
Previous Data from 2021
Water Company Name | Site Name (EA Consents Database) | Site Name (WaSC operational name) [optional] | EA Permit Reference (EA Consents Database) | WaSC supplementary Permit Ref. [optional] | Activity Reference on Permit (if >1 discharge on permit) | Storm Discharge Asset Type | Outlet Discharge NGR (EA Consents Database) | WFD Waterbody ID (Cycle 2) (discharge outlet) | WFD Waterbody Catchment Name (Cycle 2) (discharge outlet) | Receiving Water / Environment (common name) (EA Consents Database) | Shellfish Water (only populate for storm overflows with a Shellfish Water EDM requirement) | Bathing Water (only populate for storm overflows with a Bathing Water EDM requirement) | Initial EDM Commission Date | Total Duration (hrs) all spills prior to processing through 12-24h count method | Counted spills using 12-24h count method | EDM Operation - % of reporting period EDM operational | EDM Operation - Reporting % - Primary Reason <90% | EDM Operation - Action taken / planned - Status & timeframe | High Spill Frequency - Operational Review - Primary Reason | High Spill Frequeny - Action taken / planned - Status & timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic Capacity) | Updates / Comments | Total Duration (hrs) all spills prior to processing through 12-24h count method | Counted spills using 12-24h count method | EDM Operation - % of reporting period EDM operational
United Utilities | (IN SCOUT HUT) OWLEY WOOD ROAD CSO | (In Scout Hut) Owley Road CSO | 01VRY0096 | VRY0096 | SO | CSO on Sewer Network | SJ6250074270 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 72.25% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | 10 WARWICK AVENUE CSO (42058) | 10 Warwick Avenue CSO | 016920445 | STH0075 | SO | CSO on Sewer Network | SJ5901094760 | GB112069061220 | Millingford (Newton) Brook | NEWTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 465.22 | 78 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 102 MIDDLEWICH ROAD CSO | 102 Middlewich Road CSO | 016892222 | VRY0091 | SO | CSO on Sewer Network | SJ6753073600 | GB112068060370 | Wade Brook | TRIB OF WADE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 403.13 | 72 | 88.45% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | 103 BRINKSWAY/LARK HILL | 103 Brinksway/Lark Hill CSO | 016982676 | STK0114 | SO | CSO on Sewer Network | SJ8845089970 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | 11 NORTH PARK AVENUE CSO | 11 NORTH PARK AVENUE CSO | 01PEN0027 | PEN0027 | SO | CSO on Sewer Network | SD8537038380 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Commissioned in 2019 - full year data expected | 46.95 | 98 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 113 HASSALL RD CSO | HASSALL ROAD CSO | 01CON0023 | CON0023 | SO | CSO on Sewer Network | SJ7869756899 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | DAY GREEN STREAM | N/A | N/A | Commissioned in 2018 - full year data expected | 14.77 | 18 | 100%
United Utilities | 134 BURNLEY ROAD CSO | 134 Burnley Road CSO | 017180606 | PEN0079 | SO | CSO on Sewer Network | SD8668023570 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 36.81% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | 143 BURNLEY ROAD EAST CSO | 143 Burnley Road East CSO | 016993566 | ROS0026 | SO | CSO on Sewer Network | SD8371022300 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 422.6 | 62 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 161 A DICKENSON ROAD CSO | 161a Dickenson Road CSO | 016982725 | MAN0297 | SO | CSO on Sewer Network | SJ8611095130 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 3.67 | 5 | 100%
United Utilities | 18 DEEPDALE ROAD | 18 Deepdale Road CSO | 017190864 | PRE0020 | SO | CSO on Sewer Network | SD5528028741 | 176 | #N/A | RIVER RIBBLE VIA STORM CULVERT | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | 181 LONDON ROAD CSO | 181 London Road CSO | 016892203 | VRY0144 | SO | CSO on Sewer Network | SJ6594072970 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 153 | 87 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 184 WARRINGTON ROAD CSO | 184 Warrington Road CSO | EPRHB3499NK | WIG0254 | SO | CSO on Sewer Network | SD5671804467 | GB112070064820 | Douglas - Lower | TRIB OF RIVER DOUGLAS VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | 188 RATING LANE CSO | 017480404 | 017480404 | BRW0038 | SO | CSO on Sewer Network | SD2194069330 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BRIDGE/MILLBECK | WALNEY EAST | N/A | Commissioned in 2016 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | 19 WOOD LANE CSO | 19 Wood Lane (Marple) CSO | 016892515 | STK0148 | SO | CSO on Sewer Network | SJ9476088370 | GB112069061000 | Goyt (Etherow to Mersey) | TRIB TORKINGTON BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.37 | 1 | 100%
United Utilities | 194 ORMSKIRK ROAD CSO | 194 Ormskirk Road | 017081269 | WLN0048 | SO | CSO on Sewer Network | SD4875205989 | GB112070064790 | Tawd | RIVER TAWD VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 238.57 | 78 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | 2 MILL LANE COMBINED SEWER OVERFLOW | 2 Mill Lane CSO | 01PRE0031 | PRE0031 | SO | CSO on Sewer Network | SD5250031380 | GB112071065470 | Savick Brook | SAVICK BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 21.1 | 10 | 99.79%
United Utilities | 20 ADLINGTON ROAD CSO | 20 Adlington Road CSO | 016892094 | MAC0053 | SO | CSO on Sewer Network | SJ9306078000 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Commissioned in 2019 - full year data expected | 231.13 | 99 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 20 RIBBLETON DRIVE CSO | 20 Ribbleton Drive CSO | 01HYN0035 | HYN0035 | SO | CSO on Sewer Network | SD7614029920 | GB112071065490 | Calder - Pendle Water to conf Ribble | CLOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | 208 DEEPDALE ROAD CSO | 208 Deepdale Road CSO | 017180537 | PRE0106 | SO | CSO on Sewer Network | SD5453030430 | 176 | #N/A | MOOR BROOK CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 1.5 | 7 | 100%
United Utilities | 212 MOTTRAM ROAD CSO | 212 Mottram Road CSO | 01TAM0114 | TAM0114 | SO | CSO on Sewer Network | SJ9721097300 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | TRIB OF ACRES BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.4 | 4 | 100%
United Utilities | 230 LONDON ROAD CSO | 230 London Road CSO | 01VRY0074 | VRY0074 | SO | CSO on Sewer Network | SJ6598073260 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 26.37 | 30 | 100%
United Utilities | 242 STOCKPORT RD WEST | 242 Stockport Road West CSO | 01STK0002 | STK0002 | SO | CSO on Sewer Network | SJ9202091751 | GB112069061000 | Goyt (Etherow to Mersey) | CROOKILLEY BROOK CULVERT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | 250M OF ASHTON ROAD BARDSLEY PS CSO | 250 metres d/s Ashton Road (Bardsley PS) CSO | 016980030 | OLD0120 | SO | Storm Discharge at Pumping Station | SD9287001150 | GB112069061151 | Medlock (Source to Lumb Brook) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.18 | 8 | 100%
United Utilities | 258 COUNCILLOR LANE | 258 Councillor Lane CSO | 016982684 | STK0129 | SO | CSO on Sewer Network | SJ8727087710 | GB112069060940 | Micker Brook | MICKER BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 17.5 | 33 | 96.84%
United Utilities | 27/29 ABBOTSMEAD CSO | 27/29 Abbotsmead Approach CSO | 017480451 | BRW0042 | SO | CSO on Sewer Network | SD2194069331 | GB112074069790 | Mill Beck (Poaka Beck) | MILL BECK | WALNEY EAST | Walney Sandy Gap | Commissioned in 2016 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | 273 REGENT ST CSO (32013) | Rear of 273 Regent Street CSO | 01PEN0006 | PEN0006 | SO | CSO on Sewer Network | SD8681039160 | GB112071065150 | Colne Water - Wanless Water to Pendle Water | SWINDEN CLOUGH | N/A | N/A | Commissioned in 2020 - full year data expected | 169.38 | 38 | 100%
United Utilities | 28 TYTHEBARN ST | 28 Tythebarn Street CSO | 01BBN0120 | BBN0120 | SO | CSO on Sewer Network | SD6957022320 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN (SEWER) | N/A | N/A | Commissioned in 2020 - full year data expected | 4.21 | 13 | 100%
United Utilities | 28/29 ARLECDON PARKS ROAD CSO | Arlecdon Parks Road CSO to Winder Beck | 01COP0017 | COP0017 | SO | CSO on Sewer Network | NY0514018660 | GB112074070010 | Ehen (upper including Liza) | TRIB OF WINDER BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | 29 CRESSWELLSHAWE RD A CSO 13567 | 29 Cresswellshawe Road (Overflow A) CSO | 016892427 | CON0026 | SO | CSO on Sewer Network | SJ7981156068 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BRK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 267.27 | 141 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | 29 CRESSWELLSHAWE RD B CSO 13567 | 29 Cresswellshawe Road (Overflow B) CSO | 016892426 | CON0025 | SO | CSO on Sewer Network | SJ7989056280 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BRK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 5.73 | 12 | 100%
United Utilities | 293 PRESTON OLD ROAD CSO (052M0) | 293 PRESTON OLD ROAD CSO | 01BBN0045 | BBN0045 | SO | CSO on Sewer Network | SD6624026970 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 0.1 | 1 | 100%
United Utilities | 293 PRESTON OLD ROAD CSO (052M0) | Preston Old Road CSO | 01BBN0044 | BBN0044 | SO | CSO on Sewer Network | SD6624026970 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER BLAKEWATER | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | 295 BACUP ROAD CSO | 295 BACUP ROAD CSO | 01ROS0008 | ROS0008 | SO | CSO on Sewer Network | SD8195022630 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 522.7 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 3 PARK ROAD CSO | No 3 Park Road CSO | 016982965 | WIR0140 | SO | CSO on Sewer Network | SJ3718080580 | 171 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | 3 WOOD RD | 3 Wood Road CSO | 01MAN0311 | MAN0311 | SO | CSO on Sewer Network | SJ8235095200 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | OUEL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | 31 ABBOTSMEAD APPROACH CSO | 31 Abbotsmead Approach CSO | 017480449 | BRW0040 | SO | CSO on Sewer Network | SD2177069780 | GB112074069790 | Mill Beck (Poaka Beck) | MILLBECK | WALNEY EAST | N/A | Commissioned in 2016 - full year data expected | 15.13 | 24 | 99.8%
United Utilities | 310-314 CHESTER ROAD CSO | 310 -314 Chester Road CSO | 016810821 | VRY0020 | SO | CSO on Sewer Network | SJ6209072650 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | HANDFORTH BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | 329 BARTON ROAD CSO | Barton Road CSO | 016892359 | TRA0103 | SO | CSO on Sewer Network | SJ7886095300 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | BENT LANES BROOK/LONGFORD BROO | N/A | N/A | Commissioned in 2019 - full year data expected | 26.83 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 36 HIBBERT LANE CSO 431Y7 | 36 Hibbert Lane CSO | 01STK0099 | STK0099 | SO | CSO on Sewer Network | SJ9527088420 | GB112069061000 | Goyt (Etherow to Mersey) | MARPLE BRK TRIB TORKINGTON BR | n/a | n/a | Commissioned in 2018 - full year data expected | 0.23 | 1 | 100%
United Utilities | 3-8 MORNINGSIDE CSO 3282GE | 3/8 Morningside CSO | 016983112 | SEF0118 | SO | CSO on Sewer Network | SJ3332099130 | 348 | #N/A | RIMROSE BROOK, TRIB RVR MERSEY | North Wirral | n/a | Commissioned in 2017 - full year data expected | 0.07 | 1 | 100%
United Utilities | 389 HOYLAKE ROAD CSO | 389 Hoylake Road CSO | 016892440 | WIR0077 | SO | CSO on Sewer Network | SJ2549089490 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | NORTH WIRRAL (WEST) | Moreton | Commissioned in 2016 - full year data expected | 197.4 | 22 | 100%
United Utilities | 39 PARK AVENUE CSO | Park Avenue CSO | 017190821 | CHR0004 | SO | CSO on Sewer Network | SD5559018880 | GB112070064861 | Yarrow Culbeck Brook to tidal | RIVER YARROW & CHAPEL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 34.54 | 28 | 100%
United Utilities | 39 PARK AVENUE CSO | Park Avenue CSO | 017190821 | CHR0004 | SO | CSO on Sewer Network | SD5559018880 | GB112070064861 | Yarrow Culbeck Brook to tidal | RIVER YARROW & CHAPEL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 8.34 | 5 | 99.97%
United Utilities | 396 ATHERTON ROAD CSO | 396 Atherton Road CSO | 016983329 | WIG0229 | SO | CSO on Sewer Network | SD6266003630 | GB112069064520 | Hey/Borsdane Brook | DOG POOL BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 1 | 3 | 100%
United Utilities | 4 TAVLIN AVENUE CSO | 4 Tavlin Avenue CSO | 016993627 | WAR0076 | SO | CSO on Sewer Network | SJ5992089940 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | DALLAM BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 79.1 | 10 | 100%
United Utilities | 42 BRIDGE STREET CSO | 42 Bridge Street CSO | 01WIG0054 | WIG0054 | SO | CSO on Sewer Network | SD6205004610 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | 42 RUNCORN ROAD CSO | 42 Runcorn Road CSO | 016892245 | VRY0147 | SO | CSO on Sewer Network | SJ6375074630 | GB112068060500 | Weaver (Dane to Frodsham) | WEAVER NAVIGATION | N/A | N/A | Commissioned in 2020 - full year data expected | 82.6 | 48 | 89.84% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 5 CROXTON RD PS | Croxton Road (Middlewich No. 5 PS) | 01CON0011 | CON0011 | SO | Storm Discharge at Pumping Station | SJ6948066950 | GB112068055380 | Wheelock (Fowle Brook to Dane) | RIVER WHEELOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 40.53 | 6 | 99.9%
United Utilities | 50 BRIDGE LANE BRAMHALL CSO | 50 Bridge Lane CSO | 016982681 | STK0125 | SO | CSO on Sewer Network | SJ8973086300 | GB112069060940 | Micker Brook | LADY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 6.6 | 12 | 100%
United Utilities | 560 MANCHESTER ROAD CSO | 580 Manchester Road CSO | 01HYN0038 | HYN0038 | SO | CSO on Sewer Network | SD7755026110 | GB112071065040 | Hyndburn | VIA CULVERT TO WOODNOOK WATER | N/A | N/A | Commissioned in 2019 - full year data expected | 113.9 | 30 | 100%
United Utilities | 58/64 AUDLEY ROAD CSO | 58/64 Audley Road CSO | 01CON0019 | CON0019 | SO | CSO on Sewer Network | SJ7995054830 | GB112068074630 | Valley Brook (Source to Englesea Brook) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 61.6 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 59D TURVES ROAD CSO 432VY | No. 59d Turves Road CSO | 016982768 | STK0122 | SO | CSO on Sewer Network | SJ8684086520 | GB112069060940 | Micker Brook | TURVES BROOK, TRIB MICKER BRK | n/a | n/a | Commissioned in 2018 - full year data expected | 2.4 | 11 | 100%
United Utilities | 6 SANDY LANE WEST (LONGFORD) CSO | 6 Sandy Lane West (Longford) CSO | 01WAR0050 | WAR0050 | SO | CSO on Sewer Network | SJ6019090831 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | MILL BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 118.17 | 13 | 100%
United Utilities | 650YDS DS KINGWAY RVR BRIDGE CSO | 650 yards downstream of Kingsway River Bridge CSO | 01STK0019 | STK0019 | SO | CSO on Sewer Network | SJ8450089370 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2017 - full year data expected | 425.27 | 89 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | 674 RIPPONDEN ROAD CSO | Ripponden Road CSO | 016983139 | OLD0165 | SO | CSO on Sewer Network | SD9507407373 | GB112069064690 | Beal | CLVRT'D SECTION HODGE CLOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 75.87 | 23 | 99.98%
United Utilities | 709 BACUP ROAD CSO | OPPOSITE 709 BACUP ROAD CSO | 01ROS0007 | ROS0007 | SO | CSO on Sewer Network | SD8335021830 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.07 | 1 | 100%
United Utilities | 74 SLATER LANE (LEYLAND) CSO | 74 Slater Lane (Leyland) CSO | 01SRI0032 | SRI0032 | SO | CSO on Sewer Network | SD5233021570 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 255.23 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | 745 EDENFIELD ROAD CSO | 745 Edenfield Road CSO | 016997072 | ROC0188 | SO | CSO on Sewer Network | SD8583014620 | GB112069064710 | Naden Brook | NADEN BROOK TRIB OF R ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 0.13 | 2 | 99.99%
United Utilities | 75 LOWER BANK ROAD CSO | 75 LOWER BANK ROAD CSO | 01PRE0017 | PRE0017 | SO | CSO on Sewer Network | SD5409031320 | GB112071065470 | Savick Brook | EAVES BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.4 | 1 | 99.98%
United Utilities | 807 WALMERSLEY ROAD (BURY) CSO | 807 Walmersley Road (Bury) CSO | 016982618 | BRY0116 | SO | CSO on Sewer Network | SD8047013840 | GB112069064620 | Irwell (Rossendale STW to Roch) | WALMERSELY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 4.8 | 4 | 100%
United Utilities | 876 BURNLEY RD EAST CSO | 876 Burnley Road East CSO | 01ROS0006 | ROS0006 | SO | CSO on Sewer Network | SD8366024720 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | 91 MANCHESTER ROAD CSO 072GO | 91 Manchester Road CSO | 01BOL0105 | BOL0105 | SO | CSO on Sewer Network | SD7219008430 | GB112069064540 | Middle Brook | CROAL MINOR | n/a | n/a | Commissioned in 2018 - full year data expected | 256.97 | 77 | 93.06% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | 92 BURNLEY ROAD CSO 081HP | 92 Burnley Road CSO | 01BUR0010 | BUR0010 | SO | CSO on Sewer Network | SD8225028070 | GB112069064680 | Limy Water | LIMY WATER | N/A | N/A | Commissioned in 2018 - full year data expected | 189.43 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 95/97 CRAIG ROAD HEATON MERSEY CSO | 95/97 Craig Road CSO | 016982667 | STK0102 | SO | CSO on Sewer Network | SJ8726089930 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 8.03 | 44 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | 96 COLLINGWOOD ROAD CSO 121PB | 96 COLLINGWOOD ROAD CSO | 01CHR0017 | CHR0017 | SO | CSO on Sewer Network | SD5750017000 | GB112070064952 | Yarrow DS Big Lodge Water | CLVRTED TRIB RIVER CHOR | N/A | N/A | Commissioned in 2017 - full year data expected | 5 | 16 | 100%
United Utilities | 97 WOOD LANE CSO | 97 Wood Lane CSO | 016892443 | WIR0081 | SO | CSO on Sewer Network | SJ2556088180 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | A591 BUS SHELTER CSO 021BY | A591/Bus Shelter CSO | 01ALL0026 | ALL0026 | SO | CSO on Sewer Network | NY2587025070 | GB112075073561 | Derwent US Bassenthwaite Lake | APPLETHWAITE GILL | N/A | N/A | Commissioned in 2018 - full year data expected | 780.77 | 77 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ABBEY RD/HOLLOW LANE CSO | Abbey Road/Hollow Lane CSO | 017480443 | BRW0034 | SO | CSO on Sewer Network | SD2194069332 | GB112074069790 | Mill Beck (Poaka Beck) | MILLBECK | WALNEY EAST | N/A | Commissioned in 2016 - full year data expected | 850.23 | 192 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ABBEY VILLAGE PUMPING STATION | Abbey Village Pumping Station (12001) (CHR0080) | 017180377 | CHR0080 | SO | Storm Discharge at Pumping Station | SD6435022930 | GB112071065250 | Roddlesworth | RIVER RODDLESWORTH | n/a | n/a | Commissioned in 2018 - full year data expected | 404.38 | 52 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ABBEYHILLS COMBINED SEWER OVERFLOW | Abbeyhills Combined Sewer Overflow (31028) (OLD0124) | 01OLD0124 | OLD0124 | SO | CSO on Sewer Network | SD9482203177 | GB112069061151 | Medlock (Source to Lumb Brook) | CULVERT GLODWICK BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.07 | 1 | 100%
United Utilities | ABBEYHILLS COMBINED SEWER OVERFLOW | Abbeyhills Road CSO | 016982467 | OLD0151 | SO | CSO on Sewer Network | SD9482203177 | GB112069061151 | Medlock (Source to Lumb Brook) | TRIB RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.17 | 1 | 100%
United Utilities | ABBEYTOWN PUMPING STATION | Abbeytown Pumping Station (Site ID ABETW) (ALL0104) | 017580256 | ALL0104 | SO | Storm Discharge at Pumping Station | NY1778050600 | GB102075073440 | Waver | STANK BECK | SOLWAY | Silloth | Commissioned in 2018 - full year data expected | 346.69 | 39 | 100%
United Utilities | ABNEY HALL | Abney Hall CSO | 01STK0018 | STK0018 | SO | CSO on Sewer Network | SJ8570089250 | GB112069060940 | Micker Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | ABRAM HALL COMBINED SEWER OVERFLOW | Abram Hall CSO | 016982904 | WIG0216 | SO | CSO on Sewer Network | SD6055001400 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 297.67 | 69 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ABRAM HALL PUMPING STATION | Abram Hall PS | 01WIG0130 | WIG0130 | SO | Storm Discharge at Pumping Station | SD6058001410 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Commissioned in 2016 - full year data expected | 444.31 | 53 | 96.65% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ACCRINGTON ROAD CSO | Accrington Road CSO | 017180645 | BBN0157 | SO | CSO on Sewer Network | SD7110028060 | GB112071065310 | Blakewater | CLVRT'D SECTION KNUZDEN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 154.5 | 56 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ACCRINGTON SSO | Accrington CSO | 017160124 | HYN0005 | SO | CSO on Sewer Network | SD7425029430 | GB112071065040 | Hyndburn | RIVER HYNDBURN | n/a | n/a | Commissioned in 2018 - full year data expected | 537.39 | 99 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ACTON LANE COMBINED SEWER OVERFLOW | Acton Lane CSO | 016892441 | WIR0079 | SO | CSO on Sewer Network | SJ2552089270 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | NORTH WIRRAL (WEST) | Moreton | Commissioned in 2016 - full year data expected | 1.47 | 3 | 96.41%
United Utilities | ADDISON CLOSE CSO | Addison Close CSO | 017180643 | BBN0099 | SO | CSO on Sewer Network | SD6749027830 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 128.63 | 63 | 99.42% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ADELAIDE STREET CSO | Adelaide Street CSO | 016982543 | BOL0025 | SO | CSO on Sewer Network | SD7066007390 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 451.11 | 81 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ADJ DUXBURY MILL P.S. CSO ID 12006 | Adjacent Duxbury Mill Pumping Station Combined Sewer Overflow (CHR0024) | 01CHR0024 | CHR0024 | SO | CSO on Sewer Network | SD5882015660 | GB112070064951 | Yarrow US Big Lodge Water | RIVER YARROW | N/A | N/A | Commissioned in 2017 - full year data expected | 239.6 | 60 | 94.37% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ADJ POLICE STATION KING STREET CSO | ADJ POLICE STATION KING STREET CSO | 01RIB0002 | RIB0002 | SO | CSO on Sewer Network | SD7313041110 | GB112071065510 | Mearley Brook | TRIB OF PENDLETON BROOK BY SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0.37 | 5 | 100%
United Utilities | ADJACENT TO PADIHAM LEISURE CENTRE | Padiham Leisure Centre CSO | 017190925 | BUR0036 | SO | CSO on Sewer Network | SD7912033690 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 82.08 | 47 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ADLINGTON ROAD CSO (271A4) | Adlington Road (Bollington Park) CSO | 01MAC0120 | MAC0120 | SO | CSO on Sewer Network | SJ9310078010 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Commissioned in 2019 - full year data expected | 61.03 | 44 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | AGECROFT COMMERCE PARK PUMPING STN | Lamplight Way Pumping Station | 016993416 | SAL0191 | SO | Storm Discharge at Pumping Station | SD8081001050 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 170.31 | 26 | 99.64%
United Utilities | AGECROFT POWER STATION CSO | Agecroft Power Station | EPRQB3594EP | SAL0097 | SO | CSO on Sewer Network | SD8050002130 | GB112069061451 | Irwell (Croal to Irk) | THE RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 209.5 | 102 | 95.59% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | AGECROFT ROAD EAST CSO | Agecroft Road East CSO | 01BRY0045 | BRY0045 | SO | CSO on Sewer Network | SD8060002130 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA CULVERT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | AINSDALE WASTEWATER TREATMENT WORKS | AINSDALE WwTW | 016930486 | 16930486 | ST | Storm Tank at WwTW | SD3203011100 | GB112069064510 | Chisnall Brook | FINE JANES BROOK | Ribble | Southport | Commissioned in 2017 - full year data expected | 658.61 | 45 | 100% |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation
United Utilities | AINSLIE ST OXFORD ST CSO 041A9 | Ainslie Street/Oxford Street CSO | 01BRW0013 | BRW0013 | SO | CSO on Sewer Network | SD1966070550 | 344 | #N/A | ORMSGILL RESERVOIR | WALNEY EAST | N/A | Commissioned in 2016 - full year data expected | 6.43 | 41 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | AINSLIE ST/HARROGATE ST | Ainslie Street/Harrogate Street CSO | 01BRW0012 | BRW0012 | SO | CSO on Sewer Network | SD1966070551 | 344 | #N/A | ORMSGILL RES | WALNEY EAST | N/A | Commissioned in 2016 - full year data expected | 13.23 | 42 | 94.41% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | AINSLIE STREET/NEWPORT ST CSO 041A7 | Ainslie Street/Newport Street CSO | 01BRW0011 | BRW0011 | SO | CSO on Sewer Network | SD1966070552 | 344 | #N/A | ORMSGILL RES | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 93.19%
United Utilities | AINSTABLE WASTEWATER TREATMENT WORK | AINSTABLE WwTW | 017670046 | 17670046 | SO | Inlet CSO at WwTW | NY5278046432 | GB102076073940 | Eden - Eamont to tidal | POWSY SIKE, TRIB RIVER EDEN | n/a | n/a | Commissioned in 2018 - full year data expected | 162.8 | 33 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | ALBERT ROAD CSO | ALBERT ROAD CSO | 01BOL0095 | BOL0095 | SO | CSO on Sewer Network | SD7020008691 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 52.83 | 63 | 36.78% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ALBERT ROYDS STREET CSO | Albert Royds Street CSO | EPRSB3396NF | ROC0062 | SO | CSO on Sewer Network | SD9098014360 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Commissioned in 2020 - full year data expected | 154.43 | 85 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ALBERT ROYDS STREET CSO | Albert Royds Street CSO | EPRQB3591WC | ROC0064 | SO | CSO on Sewer Network | SD9100014400 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 4.17 | 13 | 91.48%
United Utilities | ALBION TERRACE CSO 071BD | ALBION TERRACE CSO | 01BOL0075 | BOL0075 | SO | CSO on Sewer Network | SD6969011210 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 388 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ALBYN STREET EAST CSO 33102 | Albyn Street East CSO | 017160851 | PRE0002 | SO | CSO on Sewer Network | SD5493029330 | 176 | #N/A | SWILLBROOK CLVRT TRIB R RIBBLE | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 74.96 | 14 | 100%
United Utilities | ALDERLEY EDGE WWTW ALDYE | ALDERLEY EDGE WwTW | 016910001 | 16910001 | SO | Inlet CSO at WwTW | SJ8283078580 | GB112069061330 | Mobberley Brook | WHITEHALL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 1992.42 | 145 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ALDERLEY EDGE WWTW CSO | Alderley Edge WwTW CSO MAC0174 | 016892364 | MAC0174 | SO | CSO on Sewer Network | SJ8302078810 | GB112069061330 | Mobberley Brook | CARR BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 886.52 | 94 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ALEXANDER DRIVE CSO | Alexander Drive CSO | 016920990 | HAL0005 | SO | CSO on Sewer Network | SJ4981085330 | 170 | #N/A | STEWARDS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 266.54 | 82 | 99.7% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ALFORD STREET PUMPING STATION | Alford Street PS | 016982210 | OLD0123 | SO | Storm Discharge at Pumping Station | SD9018002570 | GB112069061152 | Medlock (Lumb Brook to Irwell) | MOSTON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | ALLEN ST/LORD ST CSO | Allen Street/Lord Street CSO | EPRSB3793EM | MAC0054 | SO | CSO on Sewer Network | SJ9374077640 | GB112069060650 | Dean (Lamaload to Bollington) | RIVER DEAN | N/A | N/A | Commissioned in 2020 - full year data expected | 0.53 | 5 | 100%
United Utilities | ALLERBY WWTW ALLER | ALLERBY WwTW | 017570082 | 17570082 | ST | Storm Tank at WwTW | NY0892039130 | 357 | #N/A | BRUNSOW BECK | SILLOTH | Allonby South | Commissioned in 2016 - full year data expected | 360.6 | 51 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ALLONBY WWTW ALLON | ALLONBY WwTW | 017580272 | 17580272 | SO | Inlet CSO at WwTW | NY0812244142 | 357 | #N/A | IRISH SEA (ALLONBY BAY) | SILLOTH | Allonby Allonby South | Commissioned in 2017 - full year data expected | 160.44 | 11 | 99.46%
United Utilities | ALSAGER RD CSO | Alsager Road Combined Sewer Overflow (Site ID 291BO) (NEW0039) | 016882294 | NEW0039 | SO | CSO on Sewer Network | SJ7960051530 | GB112068074630 | Valley Brook (Source to Englesea Brook) | AUDLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 25.7 | 14 | 100%
United Utilities | ALSAGER STW | ALSAGER WwTW | 016810042 | 16810042 | ST | Storm Tank at WwTW | SJ7891056790 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | TRIBUTARY OF RIVER DANE | N/A | N/A | Commissioned in 2020 - full year data expected | 321.66 | 80 | 100% |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Scheduled
United Utilities | ALTHAM OUTFALL (FENNYFOLD) CSO | Altham Outfall CSO | 017160089 | BUR0026 | SO | CSO on Sewer Network | SD7883033050 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 305.09 | 70 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ALTON STREET NO 2 CSO 161BP | Alton Street No.2 CSO | 01CRE0035 | CRE0035 | SO | CSO on Sewer Network | SJ6996055310 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 211.87 | 18 | 99.97%
United Utilities | ALTON STREET NO 2 CSO 161BP | Alton Street CSO | 01CRE0035 | CRE0033 | SO | CSO on Sewer Network | SJ6996055310 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.83 | 4 | 100%
United Utilities | ALTRINCHAM RD WESTEND AVE CSO 431BS | ALTRINCHAM ROAD / WEST END AVENUE CSO | 01MAN0226 | MAN0226 | SO | CSO on Sewer Network | SJ8431088730 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | GATLEY BROOK VIA SWS | N/A | N/A | Commissioned in 2017 - full year data expected | 2.2 | 16 | 95.76%
United Utilities | ALTRINCHAM STW | ALTRINCHAM WwTW | 016940141 | 16940141 | ST | Storm Tank at WwTW | SJ7504090440 | GB112069060980 | Sinderland Brook | SINDERLAND BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | Resolved - November |  |  |  | Investigation now complete, remedial work due
United Utilities | ALTRINHAM WWTW HIGH LEVEL OVERFLOW | Altrincham WwTW High Level Overflow (Formerly Woodcote Road CSO) | 016892363 | TRA0034 | SO | Storm Discharge at Pumping Station | SJ7532090270 | GB112069060980 | Sinderland Brook | SINDERLAND BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 23.87 | 20 | 92.96%
United Utilities | ALUM BRIDGE PUMPING STATION | Alum Bridge PS | 01CON0064 | CON0064 | SO | Storm Discharge at Pumping Station | SJ7650066500 | GB112068055460 | Croco | RIVER CROCO | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | AMBLESIDE WWTW | AMBLESIDE WwTW | 017370024 | 17370024 | ST | Storm Tank at WwTW | NY3722003890 | GB112073071140 | Rothay | RIVER ROTHAY | n/a | n/a | Commissioned in 2018 - full year data expected | 1043.95 | 62 | 99.19% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Data updated June 2022 following EDM investigation | N/A | N/A | 0%
United Utilities | ANCHOR LANE CSO | Anchor Lane CSO | NPSWQD002980 | BBN0165 | SO | CSO on Sewer Network | SD6889824062 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 1875.41 | 125 | 99.92% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ANCHORSHOLME PS | Anchorsholme PS | 017160288 | BPL0040 | SO | Storm Discharge at Pumping Station | SD3118042260 | GB641211630001 | Mersey Mouth | IRISH SEA | Lune (Wyre Estuary) | Bispham, Cleveleys, Fleetwood | Commissioned in 2017 - full year data expected | 523.92 | 56 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ANDERTON FIELD NO28 | Anderton Field No. 28 | 01VRY0002 | VRY0002 | SO | Storm Discharge at Pumping Station | SJ6496076140 | GB112068060510 | Cogshall Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | ANTHORN PS ANTHN | Anthorn PS | 01ALL0035 | ALL0035 | SO | Storm Discharge at Pumping Station | NY2002058380 | GB530207614700 | SOLWAY | RIVER WAMPOOL ESTUARY | SOLWAY | Silloth | Commissioned in 2018 - full year data expected | 50.49 | 26 | 100%
United Utilities | ANYON STREET/LAUREL AVE CSO | ANYON STREET / LAUREL AVENUE CSO | 01BBN0119 | BBN0119 | SO | CSO on Sewer Network | SD6985022750 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 175.5 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | APETHORN LANE | Apethorn Lane | 016982688 | TAM0152 | SO | CSO on Sewer Network | SJ9460093470 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | APPLE STREET CSO | APPLE STREET CSO | 01BBN0040 | BBN0040 | SO | CSO on Sewer Network | SD6709027610 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 22.33 | 18 | 100%
United Utilities | APPLEBY CSO | Appleby CSO Adj to Appleby WwTW | 017680301 | EDE0097 | SO | CSO on Sewer Network | NY6766020840 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | n/a | n/a | Commissioned in 2018 - full year data expected | 117.84 | 24 | 100%
United Utilities | APPLEBY SREETT CSO | Appleby Street CSO | 017180644 | BBN0156 | SO | CSO on Sewer Network | SD6915028540 | GB112071065310 | Blakewater | TRIB OF RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 141.08 | 65 | 99.68% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | APPLEBY WWTW | APPLEBY WwTW(APPLE) (017670001) | 017670001 | 17670001 | ST | Storm Tank at WwTW | NY6753021000 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | n/a | n/a | Commissioned in 2018 - full year data expected | 77.92 | 18 | 100%
United Utilities | APPLEGARTH | Moor Lane PS / Rowton A41 CSO | 01CHE0023 | CHE0023 | SO | Storm Discharge at Pumping Station | SJ4473064730 | GB111067056930 | Finchetts Gutter | CALDY BROOK RIVER DEE | Dee | n/a | Commissioned in 2017 - full year data expected | 511.83 | 31 | 89.7%
United Utilities | AQUEDUCT ROAD CSO | Aqueduct Road CSO | NPSWQD010749 | BBN0086 | SO | CSO on Sewer Network | SD6764326436 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | ARBOUR LANE PUMPING STATION | Arbour Lane Pumping Station (50033) (WIG0029 ) | 017091563 | WIG0029 | SO | Storm Discharge at Pumping Station | SD5503009730 | GB112070064820 | Douglas - Lower | MILL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 39.66 | 18 | 100%
United Utilities | ARGYL STREET | Argyll Street CSO | 01TAM0046 | TAM0046 | SO | CSO on Sewer Network | SJ9521099000 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | COCK BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | ARKWRIGHT STREET CSO | Arkwright Street CSO | 016982739 | OLD0136 | SO | CSO on Sewer Network | SD9117004990 | GB112069061120 | Wince Brook | STOCK BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 30.72 | 30 | 99.98%
United Utilities | ARLECDON COMBINED SEWER OVERFLOW | Arlecdon CSO | 017480418 | COP0001 | SO | CSO on Sewer Network | NY0508018430 | GB112074070010 | Ehen (upper including Liza) | WINDER BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 6.5 | 11 | 100%
United Utilities | ARLECDON PARKS ROAD CSO | Arlecdon Parks Road CSO | 017480419 | COP0018 | SO | CSO on Sewer Network | NY0522018650 | GB112074070010 | Ehen (upper including Liza) | ELLER GILL | N/A | N/A | Commissioned in 2019 - full year data expected | 77.6 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ARLECDON STW | ARLECDON WwTW | 017470024 | 17470024 | SO | Inlet CSO at WwTW | NY0472019130 | GB112074070020 | Dub Beck | DUB BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 120.28 | 37 | 100%
United Utilities | ARMATHWAITE WWTW | ARMATHWAITE WwTW | 017670054 | 17670054 | SO | Inlet CSO at WwTW | NY5107046370 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | n/a | n/a | Commissioned in 2017 - full year data expected | 108.5 | 100 | 99.85% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ARNSIDE PROMENADE PUMPING STATION | Arnside Promenade Pumping Station (Site ID 39042) (LAK0002) | 017370203 | LAK0002 | SO | Storm Discharge at Pumping Station | SD4573078950 | 183 | #N/A | R. KENT ESTUARY, MORECAMBE BAY | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 220.76 | 29 | 99.98%
United Utilities | ARROWEBROOK LANE CSO | Arrowe Road / Arrowe Brook Lane CSO | 016892464 | WIR0086 | SO | CSO on Sewer Network | SJ2645086930 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK TRIB RIVER BIRKET | North Wirral East | Wallasey | Commissioned in 2016 - full year data expected | 272.05 | 108 | 72.87% | Sensor failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ARTHUR ST/MEETING HOUSE LANE CSO | Arthur Street/Meeting House Lane CSO | 017680535 | EDE0030 | SO | CSO on Sewer Network | NY5151030290 | GB102076071020 | Eamont (Upper) | THACKA BECK CLVRT VIA A SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 393.23 | 45 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ARTLE BECK COMBINED SEWER OVERFLOW | Artle Beck CSO | 017290459 | LAN0119 | SO | CSO on Sewer Network | SD5339064880 | GB112072065960 | Artle Beck | ARTLE BECK, TRIB OF RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 37.23 | 17 | 100%
United Utilities | ARTLE BECK COMBINED SEWER OVERFLOW | Artle Beck Road CSO | 017290459 | LAN0108 | SO | CSO on Sewer Network | SD5339064880 | GB112072065960 | Artle Beck | ARTLE BECK, TRIB OF RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 2.03 | 11 | 99.99%
United Utilities | ASH LANE CSO | Ash Lane | 016920541 | HAL0037 | SO | CSO on Sewer Network | SJ4770085200 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | DITTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 765.02 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ASH MEADOW PUMPING STATION | Ash Meadow Pumping Station (Site id ASHME)(LAK0100) | 017380414 | LAK0100 | SO | Storm Discharge at Pumping Station | SD4463178321 | GB531207312000 | KENT | THE KENT ESTUARY | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 315.6 | 29 | 100%
United Utilities | ASHBURTON RD/CENTRAL PARK CSO | Ashburton Road/Central Park CSO | 016982253 | TRA0080 | SO | CSO on Sewer Network | SJ7886696785 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 1.77 | 5 | 100%
United Utilities | ASHEMORES LANE LAWTON RD CSO 131CE | Ashmores Lane/Lawton Road CSO | 016892428 | CON0027 | SO | CSO on Sewer Network | SJ7989056281 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BROOK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 13.4 | 28 | 100%
United Utilities | ASHES LANE CSO | Field West of Ashes Lane CSO | 016982641 | ROC0163 | SO | CSO on Sewer Network | SD9237013250 | GB112069064690 | Beal | RIVER BEAL | n/a | n/a | Commissioned in 2018 - full year data expected | 873.5 | 65 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ASHGROVE/SOUTHFIELD DR CSO | Ash Grove/Southfield Drive CSO | 016982976 | BOL0215 | SO | CSO on Sewer Network | SD6454004230 | GB112069060820 | Westleigh Brook | CULVERTED TRIB CUNNINGHAM BRK | N/A | N/A | Commissioned in 2020 - full year data expected | 83.43 | 50 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ASHTON OLD RD MANSHAW ST CSO 281CD | ASHTON OLD ROAD / MANSHAW STREET CSO | 01MAN0204 | MAN0204 | SO | CSO on Sewer Network | SJ9014097320 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MOSS BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 1.73 | 11 | 100%
United Utilities | ASHTON-UNDER-LYNE STW | ASHTON-UNDER-LYNE WwTW | 016940085 | 16940085 | SO | Inlet CSO at WwTW | SJ9300097140 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 541.9 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ASHTON-UNDER-LYNE STW | ASHTON-UNDER-LYNE WwTW | 016940085 | 16940085 | ST | Storm Tank at WwTW | SJ9300097140 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | ASKHAM WASTEWATER TREATMENT WORKS | Askham Wastewater Treatment Works (ASKHM) (017670078) | 017670078 | 17670078 | ST | Storm Tank at WwTW | NY5183023670 | GB102076071010 | Lowther (Lower) | RIVER LOWTHER | n/a | n/a | Commissioned in 2018 - full year data expected | 1177.2 | 135 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting)
United Utilities | ASKHAM-IN-FURNESS WWTW ASKAM | ASKAM-IN-FURNESS WwTW | 017470136 | 17470136 | ST | Storm Tank at WwTW | SD2118078600 | 344 | #N/A | BLEA BECK | Duddon and Walney | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2018 - full year data expected | 4908.83 | 216 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ASKHAM-IN-FURNESS WWTW ASKAM | ASKAM-IN-FURNESS WwTW | 017470136 | 17470136 | SO | Inlet CSO at WwTW | SD2118078600 | 344 | #N/A | BLEA BECK | Duddon and Walney | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2018 - full year data expected | 398.28 | 20 | 100%
United Utilities | ASPATRIA WASTEWATER TREATMENT WORKS | ASPATRIA WwTW | 017570063 | 17570063 | ST | Storm Tank at WwTW | NY1312040280 | GB112075073640 | Ellen (lower) | RIVER ELLEN | n/a | n/a | Commissioned in 2018 - full year data expected | 937.89 | 75 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ASPIN LANE CSO 281CJ | ASPIN LANE CSO | 01MAN0031 | MAN0031 | SO | CSO on Sewer Network | SJ8421099220 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2018 - full year data expected | 30.33 | 52 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ASSHETON ROAD CSO 281CA | ASSHETON ROAD CSO | 01MAN0108 | MAN0108 | SO | CSO on Sewer Network | SJ8896099510 | GB112069061152 | Medlock (Lumb Brook to Irwell) | CLVRT TRIB OF RIVER MERSEY | N/A | N/A | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | Resolved - November |  |  |  | Investigation now complete, remedial work due
United Utilities | ASTLEY BRIDGE CSO 071WP | Astley Bridge Combined Sewer Overflow (Site ID 071WP) (BOL0056) | 016950340 | BOL0056 | SO | CSO on Sewer Network | SD7152011200 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 697.07 | 142 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ATHERTON RD DETENTION TANK | Atherton Road Detention Tank | 016983228 | WIG0222 | SO | CSO on Sewer Network | SD6256003670 | GB112069064520 | Hey/Borsdane Brook | DOG POOL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 25.32 | 11 | 100%
United Utilities | ATHLONE ROAD CSO 48062 | Athlone Road CSO | 016920452 | WAR0016A | SO | CSO on Sewer Network | SJ6037090071 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | AUDLEY RD/TALKE RD JUNCTION CSO | Audley Road and Talke Road Junction CSO | EPRQB3499WS | CON0020 | SO | CSO on Sewer Network | SJ7996755137 | GB112068074630 | Valley Brook (Source to Englesea Brook) | TRIB VALLEY BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 83.33 | 48 | 99.77% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | AUDLEY WASTEWATER TREATMENT WORKS | AUDLEY WwTW | 016810045 | 16810045 | ST | Storm Tank at WwTW | SJ7953051750 | GB112068074630 | Valley Brook (Source to Englesea Brook) | AUDLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 348.56 | 80 | 99.75% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | AUDLEY WASTEWATER TREATMENT WORKS | AUDLEY WwTW | 016810045 | 16810045 | SO | Inlet CSO at WwTW | SJ7953051750 | GB112068074630 | Valley Brook (Source to Englesea Brook) | AUDLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 668.06 | 62 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | AUSTWICK PUMPING STATION CRA0010 | Austwick SPS | EPREP3526GE | CRA0010 | SO | Storm Discharge at Pumping Station | SD7642067270 | GB112072066090 | Fen Beck | TRIB FEN BECK VIA DRYING BEDS | N/A | N/A | Commissioned in 2016 - full year data expected | 2053.53 | 106 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | AVENUE ST BREWERY ST CSO | Avenue Street/Brewery Street CSO | 016982673 | STK0109 | SO | CSO on Sewer Network | SJ8985090870 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | n/a | n/a | Commissioned in 2018 - full year data expected | 26.37 | 17 | 100%
United Utilities | B&Q CSO (101C4) | B&Q CSO | 017680294 | CAR0003 | SO | CSO on Sewer Network | NY3997055030 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Commissioned in 2020 - full year data expected | 2.7 | 9 | 100%
United Utilities | BACK OF WOODLAND DRIVE CSO | Back of Woodland Drive CSO | 01WYR0023 | WYR0023 | SO | CSO on Sewer Network | SD3522038110 | GB112072066120 | Hillylaid Pool - Tidal Wyre | UNNAMED TRIBUTARY OF MAIN DYKE | LUNE (WYRE ESTUARY) | Fleetwood | Commissioned in 2016 - full year data expected | 0.9 | 2 | 100%
United Utilities | BACK QUEENS PARK RD | Back Queen's Park Road CSO | 01BBN0055 | BBN0055 | SO | CSO on Sewer Network | SD6938027420 | GB112071065310 | Blakewater | CULVERT PRINGLE ST | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BACK TIMBERBOTTOM SPS | Longsight Park CSO | 016981480 | BOL0153 | SO | CSO on Sewer Network | SD7344011830 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 736.27 | 123 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BACUP ROAD/FALBARN FOLD CSO | Bacup Road/Markross Street CSO | 016993910 | ROS0024 | SO | CSO on Sewer Network | SD8136022670 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 641.96 | 94 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BACUP ROAD/FALBARN FOLD CSO | Highfield Road CSO | 016993910 | ROS0025 | SO | CSO on Sewer Network | SD8136022670 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 15.58 | 11 | 99.96% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BADDILEY LANE SPS | Ravensmoor PS | 016810297 | CRE0023 | SO | Storm Discharge at Pumping Station | SJ6185050450 | GB112068055250 | Edleston Brook | TRIB RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 76.29 | 26 | 99.78%
United Utilities | BAGANLEY FROOM CSO 121CW | Baganley Froom CSO | 01CHR0049 | CHR0049 | SO | CSO on Sewer Network | SD5691017960 | GB112070064952 | Yarrow DS Big Lodge Water | BLACK BROOK TRIB RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 161.87 | 33 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | BALFOUR ROAD CSO | Balfour Road CSO | 01TRA0033 | TRA0033 | SO | CSO on Sewer Network | SJ7696089540 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 2.93 | 6 | 97.18%
United Utilities | BALLAM ROAD PUMPING STATION | Ballam Road PS | 017180610 | FYL0004 | SO | Storm Discharge at Pumping Station | SD3668027570 | GB112071065650 | Liggard Brook | LIGGARD BROOK | Ribble | St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2017 - full year data expected | 77.64 | 35 | 100%
United Utilities | BALLE STREET HILTON STREET CSO | BALLE STREET / HILTON STREET CSO | 01BBN0127 | BBN0127 | SO | CSO on Sewer Network | SD6940021610 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 76.3 | 65 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BALLE STREET HILTON STREET CSO | Balle Street CSO No.1 | 01BBN0128 | BBN0128 | SO | CSO on Sewer Network | SD6940021610 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 88.17 | 65 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BALMORAL DRIVE/NORTH ROAD CSO | Balmoral Drive/North Road CSO | 01SEF0008 | SEF0008 | SO | CSO on Sewer Network | SD3715019591 | GB112070064830 | Three Pool's Waterway | RIVER RIBBLE | RIBBLE | Southport | Commissioned in 2016 - full year data expected | 693.03 | 58 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BAMFURLONG PUMPING STATION | Bamfurlong Pumping Station (50013) (WIG0127) | 01WIG0127 | WIG0127 | SO | Storm Discharge at Pumping Station | SD6012001780 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 856.26 | 62 | 99.84% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BANBURY CLOSE CSO | Banbury Close CSO | 01MAC0064 | MAC0064 | SO | CSO on Sewer Network | SJ9227074880 | GB112069061320 | Bollin (Source to Dean) | SHORESCLOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 10.2 | 25 | 100%
United Utilities | BANK LANE TINTWISTLE CSO | Bank Lane (Tintwistle) Combined Sewer Overflow | 01PEA0043 | PEA0043 | SO | CSO on Sewer Network | SK0206096980 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Commissioned in 2019 - full year data expected | 4902.75 | 205 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BANK PARADE CSO | Bank Parade CSO | 017180386 | PRE0087 | SO | CSO on Sewer Network | SD5421028660 | 176 | #N/A | RIVER RIBBLE | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BANK ST COMBINED SEWER OVERFLOW | Bank Street CSO | 016993909 | ROS0001 | SO | CSO on Sewer Network | SD8122022880 | GB112069064680 | Limy Water | LIMY WATER TRIB OF R IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 333.97 | 73 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BANK STREET CSO | BANK STREET STORAGE TANK CSO (28CSO123) | 016982847 | MAN0102 | SO | CSO on Sewer Network | SJ8749099230 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BANKBOTTOM COMBINED SEWER OVERFLOW | Bankbottom CSO | 016892347 | PEA0040 | SO | CSO on Sewer Network | SK0218096550 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | TRIBUTARY OF RIVER ETHEROW | N/A | N/A | Commissioned in 2019 - full year data expected | 1.33 | 7 | 100%
United Utilities | BANKHALL CSO 99007 LIV0038 | Bankhall Relief CSO | 016930969 | LIV0037B | SO | CSO on Sewer Network | SJ3320093500 | 167 | #N/A | RIVER MERSEY | North Wirral East | Wallasey | Commissioned in 2016 - full year data expected | 4.88 | 19 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | BANKHALL CSO 99007 LIV0038 | Bankhall CSO | 016930969 | LIV0038 | SO | CSO on Sewer Network | SJ3320093500 | 167 | #N/A | RIVER MERSEY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 1.23 | 10 | 100%
United Utilities | BANKHALL RELIEF CSO 99005 | Northern CSO | 016930968 | LIV0037A | SO | CSO on Sewer Network | SJ3300093900 | 167 | #N/A | RIVER MERSEY ESTUARINE WATERS | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 59.37 | 45 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BANKSFIELD AVENUE CSO 33027 | Banksfield Avenue CSO | 017180625 | PRE0114 | SO | CSO on Sewer Network | SD5203031250 | GB112071065470 | Savick Brook | SAVICK BRK TRIB OF RIBBLE EST | n/a | n/a | Commissioned in 2018 - full year data expected | 5.2 | 8 | 100%
United Utilities | BARDSEA SPS(TOILET BLOCK) | Toilet Block Sewage PS | 017280254 | LAK0093 | SO | Storm Discharge at Pumping Station | SD3021074320 | 181 | #N/A | BARDSEA BECK | Morecambe Bay (Leven) | n/a | Commissioned in 2017 - full year data expected | 43.44 | 5 | 99.98%
United Utilities | BARLOW MOOR RD/PALATINE RD CSO | Barlow Moor Road/Palatine Road CSO | 01MAN0236 | MAN0236 | SO | CSO on Sewer Network | SJ8346091620 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BARLOW MOOR ROAD | Barlow Moor Road / Rowsley Avenue CSO | 01MAN0244 | MAN0244 | SO | CSO on Sewer Network | SJ8329091780 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 835.27 | 95 | 93.6% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BARNABY RD CSO | Barnaby Road CSO | 016983005 | MAC0163 | SO | CSO on Sewer Network | SJ9148083790 | GB112069060900 | Poynton Brook | POYNTON BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 5.8 | 3 | 89.78%
United Utilities | BARNOLDSWICK WWTW | BARNOLDSWICK WwTW | 017160028 | 17160028 | ST | Storm Tank at WwTW | SD8785048010 | GB112071065540 | Stock Beck | STOCK BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 154.71 | 36 | 100%
United Utilities | BARNSTON STORM TANK 51070 | Barnston Storm Tanks (51CSO065) | 01WIR0095 | WIR0095 | SO | CSO on Sewer Network | SJ2857084290 | GB112068060530 | The Birket including Arrowe Brook and Fender | PRENTON BROOK | North Wirral East | N/A | Commissioned in 2016 - full year data expected | 94.53 | 29 | 83% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | BARONS QUAY PS | Barons Quay PS | 01VRY0118 | VRY0118 | SO | Storm Discharge at Pumping Station | SJ6581074270 | GB112068060500 | Weaver (Dane to Frodsham) | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BARROW LANE CSO (451G7) | Barrow Lane CSO | 01TRA0059 | TRA0059 | SO | CSO on Sewer Network | SJ7840085170 | GB112069061381 | Bollin (River Dean to Ashley Mill) | TRIB OF RIVER BOLLIN | N/A | N/A | Commissioned in 2020 - full year data expected | 103.3 | 55 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BARROWFORD CSO | Barrowford CSO | 017180569 | PEN0077 | SO | CSO on Sewer Network | SD8530038830 | GB112071065170 | Pendle Water - Colne Water to Walverden Water | PENDLE WATER | n/a | n/a | Commissioned in 2018 - full year data expected | 5.28 | 33 | 100%
United Utilities | BARROW-IN-FURNESS WWTW | Barrow-in-Furness Wastewater Treatment Works (BARFU) (017470166) | 017470166 | 17470166 | ST | Storm Tank at WwTW | SD2200068190 | 340 | #N/A | WALNEY CHANNEL | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2018 - full year data expected | 935.65 | 67 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity
United Utilities | BARROW-IN-FURNESS WWTW | Barrow-in-Furness Wastewater Treatment Works (BARFU) (017470166) | 017470166 | 17470166 | SO | Inlet CSO at WwTW | SD2200068190 | 340 | #N/A | WALNEY CHANNEL | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2018 - full year data expected | 469.21 | 57 | 28.09% | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity
United Utilities | BARROWNOOK WWTW | BARROW NOOK WwTW | 016930106 | 16930106 | SO | Inlet CSO at WwTW | SD4393001440 | GB112069060630 | Simonswood Brook | SIMONSWOOD BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BARTON LANE COMBINED SEWER OVERFLOW | Barton Lane/Fountain Street CSO | 016982648 | SAL0176 | SO | CSO on Sewer Network | SJ7677097680 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 11.37 | 12 | 100%
United Utilities | BARTON ROAD PS & CSO | Barton Road No.1 PS & No.2 CSO | 016983337 | SAL0035 | SO | CSO on Sewer Network | SJ7511099900 | GB112069061430 | Folly Brook and Salteye Brook. | WORSLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | BARTON WASTE WATER TREATMENT WORKS | BARTON WwTW | 017260043 | 17260043 | ST | Storm Tank at WwTW | SD5147035720 | GB112072065800 | Barton (Westfield) Brook | BARTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 2109.37 | 138 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BASSENTHWAITE WWTW | BASSENTHWAITE WwTW | 017570022 | 17570022 | SO | Inlet CSO at WwTW | NY2237032150 | GB112075070530 | Dash Beck | HALLS BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 51.07 | 34 | 99.99%
United Utilities | BATEMILL ROAD CSO | BATEMILL ROAD CSO | 01PEA0044 | PEA0044 | SO | CSO on Sewer Network | SK0094086910 | GB112069060970 | Sett | RIVER SETT | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | BATTERY LANE CSO | Battery Lane CSO | 016930972 | LIV0041 | SO | CSO on Sewer Network | SJ3320092000 | 167 | #N/A | MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 2.17 | 5 | 99.99%
United Utilities | BAYCLIFF PUMPING STATION 39051 | Baycliffe PS | 017370199 | LAK0001 | SO | Storm Discharge at Pumping Station | SD2905071910 | GB641211171000 | Morecambe Bay | MORECAMBE BAY ESTURIANE WATERS | Morcambe Bay (Leven) | N/A | Commissioned in 2016 - full year data expected | 905.61 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BAZIL LANE PUMPING STATION | Bazil Lane PS | NPSWQD010716 | LAN0034 | SO | Storm Discharge at Pumping Station | SD4411057280 | 343 | #N/A | CHAPEL POOLTRIB LUNE ESTUARY | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 35.1 | 15 | 100%
United Utilities | BEACONS GUTTER SSO | Beacons Gutter CSO | 016930971 | LIV0040 | SO | CSO on Sewer Network | SJ3320092700 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 2.06 | 13 | 99.92%
United Utilities | BEAM BRIDGE PUMPING STATION | Beam Bridge PS | 016810192 | CRE0022 | SO | Storm Discharge at Pumping Station | SJ6515053560 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Commissioned in 2019 - full year data expected | 1231.61 | 97 | 99.83% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BEAUMONT BUILDING CSO 28049 | Beaumont Building, Jnt New Bridge Street / Great Ducie Street CSO | 016993837 | MAN0051 | SO | CSO on Sewer Network | SJ8368099050 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 84.7 | 47 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BEECH BRIDGE SOUTH CSO | BEECH BRIDGE SOUTH CSO | 01MAC0126 | MAC0126 | SO | CSO on Sewer Network | SJ9149074550 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BEECH GROVE CSO | Beech Grove CSO | 01SAL0059 | SAL0059 | SO | CSO on Sewer Network | SD7144004040 | GB112069061100 | Astley Brook (Mersey) | TRIB HONKSFORD BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 1.77 | 12 | 100%
United Utilities | BEECH HILL LANE CSO 50089 | Beech Hill Lane CSO | 017081372 | WIG0224 | SO | CSO on Sewer Network | SD5630007360 | GB112070064820 | Douglas - Lower | BILLY PIT BROOK LPOOL CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 29.11 | 4 | 43.74% | Sensor failure / issue | Resolved - December
United Utilities | BEECH ROAD/CLAUDE RAOD CSO | Beech Road/Claude Road CSO | 016993509 | MAN0325 | SO | CSO on Sewer Network | SJ8192093240 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.63 | 4 | 75.69% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | BEECHWOOD AVENUE CSO | Beechwood Avenue CSO | 016982989 | WIR0144 | SO | CSO on Sewer Network | SJ2905092100 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 0.13 | 1 | 100%
United Utilities | BEECHWOOD ROAD CSO | Beechwood Road CSO | EPRBP3624GH | BBN0034 | SO | CSO on Sewer Network | SD6945029050 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 10.1 | 14 | 100%
United Utilities | BEHIND 33 THE ORCHARD CSO 123KF | Behind 33 The Orchard CSO | 01CHR0008 | CHR0008 | SO | CSO on Sewer Network | SD4910019080 | GB112070064912 | Lostock DS Farington Weir | TRIB OF RIVER LOSTOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 70.73 | 24 | 100%
United Utilities | BEHIND LAGER STORE CSO (174LJ) | CSO behind Lager's Store | 01EDE0022 | EDE0022 | SO | CSO on Sewer Network | NY5471039590 | GB102076073940 | Eden - Eamont to tidal | HARROW BECK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 59 | 70 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BELFIELD ROAD/BESWICKE ROYDS ST CSO | Bellfield Road/Beswicke Royds Street | EPRQB3592VZ | ROC0069 | SO | CSO on Sewer Network | SD9086014030 | GB112069064720 | Roch (Source to Spodden) | SANNEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 77.7 | 57 | 95.43% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BELGRAVE ROAD CSO | Belgrave Road CSO | 017180472 | BBN0147 | SO | CSO on Sewer Network | SD6890021810 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 4.53 | 6 | 100%
United Utilities | BELLE VUE /COCKERMOUTH PS | Belle Vue (Cockermouth) PS | 017580263 | ALL0112 | SO | Storm Discharge at Pumping Station | NY1025031180 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 299.1 | 60 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BELMONT WWTW | BELMONT WwTW | 016950031 | 16950031 | SO | Inlet CSO at WwTW | SD6833015750 | GB112069064570 | Eagley Brook | EAGLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | BENTCLIFFE WAY/WOOD ST CSO | Bentcliffe Way / Wood Street CSO | 01SAL0022 | SAL0022 | SO | CSO on Sewer Network | SJ7815098360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.2 | 4 | 100%
United Utilities | BERESFORD ROAD CSO | Beresford Road Combined Sewer Overflow | 016942057 | MAN0234 | SO | CSO on Sewer Network | SJ8655095240 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | CLVRT SECTION OF GORE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 5.47 | 13 | 100%
United Utilities | BERISFORDS COMPOUND CSO 131G3 | BERISFORDS COMPOUND CSO | 01CON0029 | CON0029 | SO | CSO on Sewer Network | SJ8650063570 | GB112068055360 | Biddulph Brook | DANE IN SHAW BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 160.8 | 53 | 98.27% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BERRYS LANE COMBINED SEWER OVERFLOW | Berrys Lane | 016982532 | STH0060 | SO | CSO on Sewer Network | SJ5347094380 | GB112069061170 | Sutton Brook | SUTTON BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 70.67 | 27 | 91.4%
United Utilities | BESWICK ST ASHTON NEW RD CSO 281D0 | Beswick Street/Ashton New Road CSO | 016982710 | MAN0256 | SO | CSO on Sewer Network | SJ8597098460 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.99%
United Utilities | BETLEY WASTE WATER TREATMENT WORKS | BETLEY WwTW | 016810049 | 16810049 | ST | Storm Tank at WwTW | SJ7500048200 | GB112068055280 | Wistaston Brook | MERE GUTTER | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | BEWSEY BRIDGE PUMPING STN | Bewsey Bridge PS | NPSWQD006951 | WAR0034 | SO | Storm Discharge at Pumping Station | SJ5923089440 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | Sankey Brook | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | BEXTON ROAD COMBINED SEWER OVERFLOW | Bexton Road CSO | 01MAC0001 | MAC0001 | SO | CSO on Sewer Network | SJ7320077500 | GB112068060410 | Smoker Brook (Gale Brook to Wincham Brook) | SERPENTINE WATER | N/A | N/A | Commissioned in 2018 - full year data expected | 90.93 | 48 | 89.76% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BICKERSHAW LANE CSO 501D5 | Bickershaw Lane Opposite Pear Tree CSO | 016982784 | WIG0204 | SO | CSO on Sewer Network | SD6161002240 | GB112069064520 | Hey/Borsdane Brook | TRIB BROOKSIDE BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 33.9 | 25 | 100%
United Utilities | BICKERSHAW LANE PUMPING STATION | Bickershaw Lane PS | 01WIG0128 | WIG0128 | SO | Storm Discharge at Pumping Station | SD6085002380 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 375.89 | 56 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BICKERSTAFFE W.WATER PUMP STATION | Bickerstaffe Wastewater PS | 016930107 | WLN0059 | SO | Storm Discharge at Pumping Station | SD4373004370 | GB112069060640 | Downholland (Lydiate/Cheshires Lines) Brook | BICKERSTAFFE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BIDDULPH WASTEWATER TREATMENT WORKS | BIDDULPH WwTW | 016810052 | 16810052 | SO | Inlet CSO at WwTW | SJ8867058860 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 196.54 | 39 | 99.95%
United Utilities | BIDDULPH WASTEWATER TREATMENT WORKS | BIDDULPH WwTW | 016810052 | 16810052 | ST | Storm Tank at WwTW | SJ8867058860 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 241.27 | 17 | 43.55% | Sensor failure / issue | Resolved - August
United Utilities | BIDSTON BY-PASS CSO | Bidston Bypass CSO | 016892425 | WIR0070 | SO | CSO on Sewer Network | SJ2845090890 | GB112068060530 | The Birket including Arrowe Brook and Fender | THE RIVER BIRKETT | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 4: No cost beneficial solution | Investigation now complete, remedial work due
United Utilities | BIGGAR VILLAGE PUMPING STATION | Biggar Village PS | 01BRW0001 | BRW0001 | SO | Storm Discharge at Pumping Station | SD1916066320 | 340 | #N/A | WALNEY CHANNEL | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 0.24 | 1 | 99.97%
United Utilities | BILLINGE HIGHER END SPS | Billinge Road/Victoria Street CSO | 017081132 | WIG0245 | SO | CSO on Sewer Network | SD5328003840 | GB112070061600 | Smithy Brook | SMITHY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.2 | 2 | 100%
United Utilities | BILLINGE SOUTH PS | BILLINGE SOUTH PUMPING STATION | 016920126 | STH0125 | ST | Storm Discharge at Pumping Station | SJ5238099020 | GB112069061230 | Black Brook (Mersey Estuary) | TRIB BLACK BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 116.23 | 45 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BILLINGE SOUTH PS | BILLINGE SOUTH PUMPING STATION | 016920126 | STH0125 | SO | Storm Discharge at Pumping Station | SJ5238099020 | GB112069061230 | Black Brook (Mersey Estuary) | TRIB BLACK BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | BILLINGTON WWTW | BILLINGTON WwTW | 017160003 | 17160003 | ST | Storm Tank at WwTW | SD7160036600 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2019 - full year data expected | 2995.35 | 157 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BILLY'S LANE CSO | Billy's Lane CSO | 016982767 | STK0121 | SO | CSO on Sewer Network | SJ8703086160 | GB112069060940 | Micker Brook | TURVES BROOK,TRIB MICKER BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 77.52 | 44 | 88.74% | Sensor failure / issue | Resolved - October | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BINNS STREET CSO | BINNS STREET CSO | 01TAM0123 | TAM0123 | SO | CSO on Sewer Network | SJ9534098130 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BIRCH HALL LN THORESWAY RD CSO | Birch Hall Lane/Thoresway Road CSO | 01MAN0245 | MAN0245 | SO | CSO on Sewer Network | SJ8633095170 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.77 | 4 | 100%
United Utilities | BIRKENHEAD WWTW BIRKE | BIRKENHEAD WwTW | 016993399 | 16993399 | ST | Storm Tank at WwTW | SJ3292089490 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY/R.BIRKET | NORTH WIRRAL (EAST) | Moreton and Wallasey | Commissioned in 2016 - full year data expected | 1992.34 | 142 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BIRKENHEAD WWTW BIRKE | BIRKENHEAD WwTW | 016993399 | 16993399 | SO | Inlet CSO at WwTW | SJ3292089490 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY/R.BIRKET | NORTH WIRRAL (EAST) | Moreton and Wallasey | Commissioned in 2016 - full year data expected | 266.02 | 59 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BIRKENHEAD WWTW BIRKE | BIRKENHEAD WwTW | 016993399 | 16993399 | SO | Inlet CSO at WwTW | SJ3292089490 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY/R.BIRKET | NORTH WIRRAL (EAST) | Moreton and Wallasey | Commissioned in 2016 - full year data expected | 0 | 0 | 99.82%
United Utilities | BIRTENSHAW FARM CSO | Birtenshaw Farm CSO (BOL0151) | 016983224 | BOL0151 | SO | CSO on Sewer Network | SD7257012620 | GB112069064570 | Eagley Brook | EAGLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 384.51 | 94 | 99.87% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BLACK BULL MH C1 CSO 331EQ | Black Bull Lane M/H C1 | EPRKB3991VZ | PRE0053 | SO | CSO on Sewer Network | SD5285631518 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 6.77 | 2 | 100%
United Utilities | BLACK HORSE HILL CSO 511EV | Black Horse Hill CSO | 016892458 | WIR0017 | SO | CSO on Sewer Network | SJ2294087780 | GB112068060530 | The Birket including Arrowe Brook and Fender | NEWTON BROOK TRIB OF R.BIRKET | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | BLACKBURN RD HALLIWELL RD CSO 071EU | Blackburn Road/Halliwell Road CSO | 01BOL0086 | BOL0086 | SO | CSO on Sewer Network | SD7163010290 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Commissioned in 2018 - full year data expected | 0.03 | 1 | 100%
United Utilities | BLACKBURN WWTW | BLACKBURN WwTW | 017160024 | 17160024 | ST | Storm Tank at WwTW | SD6047029410 | GB112071065300 | Darwen - conf Roddlesworth to tidal | HOLE BROOK & RIVER DARWEN | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2017 - full year data expected | 546.64 | 54 | 99.97% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled
United Utilities | BLACKFRIARS STREET CSO 283J1 | BLACKFRIARS STREET CSO | 01MAN0156 | MAN0156 | SO | CSO on Sewer Network | SJ8368098590 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 12.9 | 23 | 99.99% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BLACKMOOR ROAD CSO | Blackmoor Road CSO | NPSWQD010939 | CHR0063 | SO | CSO on Sewer Network | SD4825015290 | GB112070064820 | Douglas - Lower | NEW REED BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 48.11 | 61 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BLACKPOOL OLD ROAD CSO | Blackpool Old Road CSO | 017290529 | WYR0018 | SO | CSO on Sewer Network | SD3372038940 | 180 | #N/A | HORSEBRIDGE DYKE, TRIB OF MAIN | N/A | N/A | Commissioned in 2016 - full year data expected | 3.7 | 80 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BLACKPOOL ROAD CSO | Blackpool Road CSO | 01PRE0029 | PRE0029 | SO | CSO on Sewer Network | SD4928030090 | 176 | #N/A | TRIB OF THE RIVER RIBBLE | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 277.5 | 84 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BLACKSHAW LANE CSO 072FW | Blackshaw Lane CSO | 01BOL0104 | BOL0104 | SO | CSO on Sewer Network | SD7020008690 | GB112069064540 | Middle Brook | MIDDLE BROOK (RIVER CROAL) | n/a | n/a | Commissioned in 2017 - full year data expected | 28.43 | 48 | 94.91% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BLACKWOOD ROAD CSO | Blackwood Road | 01ROS0031 | ROS0031 | SO | CSO on Sewer Network | SD8527021620 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.07 | 1 | 100%
United Utilities | BLENCARN WWTW | BLENCARN WwTW | 017670047 | 17670047 | SO | Inlet CSO at WwTW | NY6349031480 | GB102076073800 | Briggle Beck | BLENCARN BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BLENCOGO PS | Blencogo WwPS | 017580267 | ALL0116 | SO | Storm Discharge at Pumping Station | NY1991048000 | GB102075073440 | Waver | TRIB RIVER WAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 25.1 | 10 | 73.31% | Sensor failure / issue | Resolved - December
United Utilities | BLENNERHASSET WW PUMPING STATION | Blennerhassett Ww PS | 017570109 | ALL0061 | SO | Storm Discharge at Pumping Station | NY1753041430 | GB112075073650 | Ellen (middle) | RIVER ELLEN | n/a | n/a | Commissioned in 2018 - full year data expected | 2612.8 | 146 | 97.73% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | BLENNERHASSET WWTW BLENN | BLENNERHASSET WwTW | 017570065 | 17570065 | ST | Storm Tank at WwTW | NY1706041460 | GB112075073650 | Ellen (middle) | RIVER ELLEN | n/a | n/a | Commissioned in 2018 - full year data expected | 1032.85 | 78 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BLIND LANE CSO 02627 | Blind Lane CSO | 017580238 | COP0089 | SO | CSO on Sewer Network | NY0083014640 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | n/a | Seascale | Commissioned in 2017 - full year data expected | 450.17 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery
United Utilities | BLINDCRAKE WWTW | Blindcrake Wastewater Treatment Works (BLIND) (017570023) | 017570023 | 17570023 | ST | Storm Tank at WwTW | NY1494034380 | GB112075073562 | Derwent DS Bassenthwaite Lake | GILL BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 1179.93 | 91 | 99.94% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | BOARDSHAW ROAD CSO | Boardshaw Road CSO | 016950217 | ROC0141 | SO | CSO on Sewer Network | SD8752006470 | GB112069061161 | Irk (Sourtce to Wince Brook) | WHIT BROOK, TRIB OF RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.67 | 1 | 99.97%
United Utilities | BOARSHAW ROAD CSO | BOARSHAW ROAD CSO | 01ROC0013 | ROC0013 | SO | CSO on Sewer Network | SD8759006660 | GB112069061161 | Irk (Sourtce to Wince Brook) | WHIT BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 75.17 | 61 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BOLLIN WALK CSO 27074 | The Wilmslow Park Road CSO | 016993490 | MAC0165 | SO | CSO on Sewer Network | SJ8529081230 | GB112069061320 | Bollin (Source to Dean) | WHITFIELD BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 51.13 | 26 | 99.98%
United Utilities | BOLTON LOW HOUSES CSO | Bolton Low Houses CSO | 017580313 | ALL0014 | SO | CSO on Sewer Network | NY2391044530 | GB102075073440 | Waver | RIVER WAVER | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | BOLTON LOW HOUSES STW | BOLTON LOW HOUSES WwTW | 017570012 | 17570012 | ST | Storm Tank at WwTW | NY2374044630 | GB102075073440 | Waver | RIVER WAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 1160.46 | 119 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | BOLTON PENRITH WWTW | BOLTON (PENRITH) WwTW | 017670002 | 17670002 | SO | Inlet CSO at WwTW | NY6428023440 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | n/a | n/a | Commissioned in 2018 - full year data expected | 381.03 | 71 | 99.98% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | BOLTON RD CANUTE STREET CSO | Bolton Road/Canute Street CSO | 01BRY0027 | BRY0027 | SO | CSO on Sewer Network | SD7792006830 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 319.84 | 103 | 72.76% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BOLTON ROAD COMBINED SEWER OVERFLOW | Bolton Road CSO | NPSWQD010684 | BBN0023 | SO | CSO on Sewer Network | SD6769026340 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | UNNAMED TRIB OF RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 40.87 | 49 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BOLTON ROAD CSO | Bolton Road CSO | 01BBN0105 | BBN0105 | SO | CSO on Sewer Network | SD6952021260 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | UNNAMED TRIB OF RIVER DARWEN | n/a | n/a | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BOLTON ROAD CSO | Bolton Road CSO | 017180468 | BBN0142 | SO | CSO on Sewer Network | SD6959021070 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | BOLTON ROAD SSO | Bolton Road CSO | 01BBN0133 | BBN0133 | SO | CSO on Sewer Network | SD7418016260 | GB112069064580 | Bradshaw Brook | 0 | n/a | n/a | Commissioned in 2018 - full year data expected | 415.3 | 54 | 93.7% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BOLTON ROAD/ASTLEY STREET CSO | Coal Pit Lane CSO | 017190911 | OLD0102 | SO | CSO on Sewer Network | SD6950021290 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | KEBBS BROOK,TRIB OF RIV DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 32.77 | 21 | 99.98%
United Utilities | BOLTON ROAD/ASTLEY STREET CSO | Bolton Road/ Astley Street CSO | 017190911 | BBN0164 | SO | CSO on Sewer Network | SD6950021290 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | KEBBS BROOK,TRIB OF RIV DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 1.86 | 9 | 100%
United Utilities | BOLTON WASTEWATER TREATMENT WORKS | BOLTON WwTW | 016950032 | 16950032 | SO | Inlet CSO at WwTW | SD7655004690 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation |  | Investigation now complete, remedial work due
United Utilities | BOLTON WASTEWATER TREATMENT WORKS | BOLTON WwTW | 016950032 | 16950032 | ST | Storm Tank at WwTW | SD7655004690 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | BOND ST CSO | Bond Street CSO | EPRQB3592AV | ROC0065 | SO | CSO on Sewer Network | SD9049014580 | GB112069064720 | Roch (Source to Spodden) | HEY BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | BONGS ROAD COMBINED SEWER OVERFLOW | Bongs Road CSO | 016892302 | STK0147 | SO | CSO on Sewer Network | SJ9329689008 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2019 - full year data expected | 146.87 | 46 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BONGS VALLEY PUMPING STATION | Bongs Valley PS | 016983106 | STK0142 | SO | Storm Discharge at Pumping Station | SJ9321089140 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2019 - full year data expected | 151.47 | 37 | 99.55%
United Utilities | BOOTH RD | Booth Road | 01ROS0074 | ROS0074 | SO | CSO on Sewer Network | SD8360022100 | GB112069064670 | Whitewell Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BOOTHROYDEN ROAD CSO | Boothroyden Road CSO | 016993590 | ROC0018 | SO | CSO on Sewer Network | SD8498004970 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 426.32 | 101 | 99.88% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BOOTHS BANK FARM CSO (37046) | Booths Bank Farm CSO | 016982745 | SAL0156 | SO | CSO on Sewer Network | SD7320000500 | GB112069061090 | Shaw Brook | SHAW BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 315.23 | 66 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BOOTLE NORTHERN OPC CSO 99102 | Bootle Northern OPC Combined Sewer Overflow | 016931013 | SEF0106 | SO | CSO on Sewer Network | SJ3210095600 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 1.28 | 13 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | BOOTLE WASTEWATER TREATMENT WORKS | BOOTLE WwTW | 017470043 | 17470043 | ST | Storm Tank at WwTW | SD0995088280 | GB112074069720 | Annas | RIVER ANNAS, SYKE BECK | N/A | Silecroft | Commissioned in 2016 - full year data expected | 278.84 | 33 | 100%
United Utilities | BORSDANE BROOK (HINDLEY) CSO | Borsdane Brook (Hindley) CSO | 016983226 | WIG0049 | SO | CSO on Sewer Network | SD6085002400 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 384.8 | 70 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BOTHEL WASTEWATER TREATMENT WORKS | BOTHEL WwTW | 017570066 | 17570066 | SO | Inlet CSO at WwTW | NY1825039470 | GB112075073640 | Ellen (lower) | BOTHEL BECK (GILL GOODEN) | n/a | n/a | Commissioned in 2018 - full year data expected | 829.5 | 127 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BOUNDARY PARK ROAD CSO | BOUNDARY PARK ROAD CSO | 01OLD0033 | OLD0033 | SO | CSO on Sewer Network | SD9063006910 | GB112069061161 | Irk (Sourtce to Wince Brook) | PLUMPTON CLOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 3.97 | 10 | 100%
United Utilities | BOUSTEADS GRASSINGS CSO | Bousteads Grassing CSO | 01CAR0049 | CAR0049 | SO | CSO on Sewer Network | NY3982054470 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | n/a | n/a | Commissioned in 2018 - full year data expected | 250.61 | 63 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | BOWDEN LANE CSO 211FL | Bowden Lane CSO | 016940364 | PEA0025 | SO | CSO on Sewer Network | SK0597181521 | GB112069060910 | Black Brook (Upper Mersey) | BLACK BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 373.63 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BOWDON WASTEWATER TREATMENT WORKS | BOWDON WwTW | 016940002 | 16940002 | ST | Storm Tank at WwTW | SJ7495085600 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | N/A | N/A | Commissioned in 2019 - full year data expected | 2008.79 | 119 | 65.88% | Sensor failure / issue | Resolved - May | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation
United Utilities | BOWNESS-ON-SOLWAY PUMPING STATION | Bowness on Solway PS | 017680457 | ALL0136 | SO | Storm Discharge at Pumping Station | NY2251162891 | 90 | #N/A | THE SOLWAY FIRTH | Solway | n/a | Commissioned in 2017 - full year data expected | 426.2 | 39 | 100%
United Utilities | BRADELEY HALL ROAD CSO | Bradeley Hall Road CSO | 016810325 | CRE0027 | SO | CSO on Sewer Network | SJ7283056220 | GB112068055400 | Fowle Brook | FOWLE BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 78.97 | 35 | 99.81%
United Utilities | BRADFIELD AVENUE CSO 318FN | BRADFIELD AVENUE CSO | 01SEF0011 | SEF0011 | SO | CSO on Sewer Network | SJ3718099520 | GB112069061441 | Alt US Bull Bridge | MOOR HEY BROOK TRIB RVR ALT | N/A | N/A | Commissioned in 2018 - full year data expected | 11.63 | 9 | 100%
United Utilities | BRADFORD ROAD | Swinton Eccles Transfer Sewer Stage 1 | 01SAL0144 | SAL0144 | SO | CSO on Sewer Network | SJ7742099920 | GB112069061430 | Folly Brook and Salteye Brook. | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BRADLEY LANE (SRETFORD) CSO | Bradley Lane CSO | 016982547 | WIG0166 | SO | CSO on Sewer Network | SJ7787093460 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2020 - full year data expected | 242.04 | 86 | 71.46% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BRADLEY LANE (SRETFORD) CSO | Bradley Lane (Stretford) CSO | 016982547 | TRA0036 | SO | CSO on Sewer Network | SJ7787093460 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2020 - full year data expected | 480.34 | 67 | 99.91% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BRADLEY ROAD CSO (328N5) | BRADLEY ROAD CSO | 01PEN0010 | PEN0010 | SO | CSO on Sewer Network | SD8619038170 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 99.92%
United Utilities | BRADSHAW STREET CSO | Bradshaw Street CSO | 017091489 | WIG0014 | SO | CSO on Sewer Network | SD5877006570 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 25.6 | 30 | 99.11%
United Utilities | BRADWELL AVENUE CSO | Bradwell Avenue CSO (451HA) (TRA0068) | 016940228 | TRA0068 | SO | CSO on Sewer Network | SJ7854095610 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK TRIB SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 2.57 | 8 | 100%
United Utilities | BRAITHWAITE WW PUMPING STATION | Braithwaite Ww PS | 01ALL0056 | ALL0056 | SO | Storm Discharge at Pumping Station | NY2365024400 | GB112075070440 | Newlands Beck | HALLGARTH BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 814.57 | 99 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | BRAMHALL ISLAND CSO | Bramhall Island CSO | EPRQB3595AJ | STK0033 | SO | CSO on Sewer Network | SJ8926086360 | GB112069060940 | Micker Brook | 0 | N/A | N/A | Commissioned in 2019 - full year data expected | 17.73 | 18 | 100%
United Utilities | BRAMHALL LN STH (NO 221) | Bramhall Lane South (No 221) | 01STK0017 | STK0017 | SO | CSO on Sewer Network | SJ8934086480 | GB112069060940 | Micker Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BRAMHALL PARK CSO | Bramhall Park CSO | EPRQB3594WA | STK0027 | SO | CSO on Sewer Network | SJ8648086790 | GB112069060940 | Micker Brook | LADY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 179.49 | 54 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BRANTHWAITE PUMPING STATION | Branthwaite PS | 017580264 | ALL0113 | SO | Storm Discharge at Pumping Station | NY0596024930 | GB112075070540 | Marron | RIVER MARRON | n/a | n/a | Commissioned in 2018 - full year data expected | 21.47 | 4 | 100%
United Utilities | BRAYSTONES WWTW | BRAYSTONES WwTW | 017470152 | 17470152 | SO | Inlet CSO at WwTW | NY0076005070 | GB112074069980 | Ehen (lower) | IRISH SEA | N/A | Seascale | Commissioned in 2016 - full year data expected | 598.3 | 158 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BREDBURY UID CSO TANK | BREDBURY UID CSO | NPSWQD010894 | STK0011 | SO | CSO on Sewer Network | SJ9208991712 | GB112069061000 | Goyt (Etherow to Mersey) | CROOKILLEY BROOK VIA A SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 17.04 | 6 | 99.97%
United Utilities | BRENTFORD STREET CSO | BRENTFORD STREET CSO | 01MAN0127 | MAN0127 | SO | CSO on Sewer Network | SD8610001200 | GB112069061131 | Irk (Wince to Irwell) | UNNAMED WATERCOURSE | N/A | N/A | Commissioned in 2018 - full year data expected | 502.03 | 39 | 99.99%
United Utilities | BRIARLANDS CL CSO AKA 4 ACK LANE | Briarlands Close CSO (formerly known as Rear of 40 Ack Lane CSO) | 016982769 | STK0123 | SO | CSO on Sewer Network | SJ8907084740 | GB112069060940 | Micker Brook | CARRWOOD PK BROOK TRIB LADY B | n/a | n/a | Commissioned in 2018 - full year data expected | 195.67 | 65 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BRIDEKIRK WWTW BRIDE | BRIDEKIRK WwTW | 017570026 | 17570026 | SO | Inlet CSO at WwTW | NY1155033800 | GB112075073570 | Broughton Beck | BRIDES BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 92.96 | 41 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BRIDGE END CSO 151F5 | Bridge End CSO | 017190756 | CRA0004 | SO | CSO on Sewer Network | SD8167564085 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | R RIBBLE VIA A SURFACE W SEWER | n/a | n/a | Commissioned in 2018 - full year data expected | 11.3 | 10 | 100%
United Utilities | BRIDGE END IND ESTATE PS | Bridge End Ind Estate Pumping Station (Site ID 02563) (COP0016) | 01COP0016 | COP0016 | SO | Storm Discharge at Pumping Station | NY0124009990 | GB112074069980 | Ehen (lower) | RIVER EHEN | n/a | Seascale | Commissioned in 2019 - full year data expected | 435.7 | 33 | 95.28%
United Utilities | BRIDGE END IND ESTATE PS | Hindburn Bridge PS | 01COP0016 | LAN0047 | SO | Storm Discharge at Pumping Station | NY0124009990 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | BRIDGE HALL LANE CSO | Bridge Hall Lane CSO | 01BRY0065 | BRY0065 | SO | CSO on Sewer Network | SD8223010640 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | BRIDGE LANE QUAYSIDE CSO | Bridge Lane | 016881727 | VRY0140 | SO | CSO on Sewer Network | SJ5296078430 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Commissioned in 2019 - full year data expected | 43.2 | 9 | 100%
United Utilities | BRIDGE RD JCT COPY LANE | Dunning's Bridge Road, Junction Copy Lane CSO | 01SEF0010 | SEF0010 | SO | CSO on Sewer Network | SJ3696099830 | GB112069061441 | Alt US Bull Bridge | MOOR HEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BRIDGE ST WEST CSO (281F9) | Bridge Street West CSO | 016993550 | MAN0174 | SO | CSO on Sewer Network | SJ8332098360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | THE RIVER IRWELL | N/A | N/A | Commissioned in 2020 - full year data expected | 0.1 | 1 | 70.12% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | BRIDGE STREET CSO | Bridge Street/Bow Street CSO | 016982898 | BOL0099 | SO | CSO on Sewer Network | SJ8333098360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 186.74 | 84 | 99.87% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BRIDGE STREET CSO | Bridge Street CSO | 016982898 | MAN0392 | SO | CSO on Sewer Network | SJ8333098360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 0.17 | 2 | 100% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BRIDGEGATE AVENUE MANHOLE 5800 CSO | Bridgegate Avenue (manhole 5800) CSO | 01BRW0041 | BRW0041 | SO | CSO on Sewer Network | SD2194069333 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSEBRIDGE/MILLBECK | Walney and Roose Beck | n/a | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | Stage 1c: Confirmed "hydraulic issue" | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | BRIDGEMAN PARK CSO | Bridgeman Park Combined Sewer Overflow | 016982924 | BOL0209 | SO | CSO on Sewer Network | SD7228008810 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Commissioned in 2020 - full year data expected | 668.89 | 31 | 68.02% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | BRIDGEMAN ST HIGHER SWAN LANE CSO | Bridgeman Street/Higher Swan Lane CSO | 01BOL0116 | BOL0116 | SO | CSO on Sewer Network | SD7087007540 | GB112069064540 | Middle Brook | JENNY BECK | N/A | N/A | Commissioned in 2018 - full year data expected | 0.03 | 1 | 98.61%
United Utilities | BRIDGEMONT COMBINED SEWER OVERFLOW | Bridgemont CSO | 016982970 | PEA0090 | SO | CSO on Sewer Network | SK0155082350 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | BRIERFIELD SSO | Clitheroe Road CSO | 017160098 | PEN0058 | SO | CSO on Sewer Network | SD8402036360 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 453.15 | 95 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BRIGHAM PUMPING STATION (ALL0138) | Brigham Pumping Station | EPRJB3597NK | ALL0138 | SO | Storm Discharge at Pumping Station | NY0838630592 | GB112075070520 | Derwent - conf Cocker to tidal | STONY BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 144.43 | 34 | 100%
United Utilities | BRIGHTON ROAD CSO | Brighton Road CSO | 016982678 | STK0116 | SO | CSO on Sewer Network | SJ8811089990 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2016 - full year data expected | 292.7 | 236 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BRINKSWAY BRIDGE/GVILLE STREET CSO | Brinksway Bridge/Grenville Street CSO | 016982764 | STK0113 | SO | CSO on Sewer Network | SJ8850090020 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 14.43 | 6 | 100%
United Utilities | BRINNINGTON RISE CSO 431GD | Brinnington Rise CSO | 016940358 | STK0038 | SO | CSO on Sewer Network | SJ9064091850 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 11.03 | 8 | 100%
United Utilities | BRISCOE DRIVE CSO 511G9 | Briscoe Drive CSO | 016881734 | WIR0126 | SO | CSO on Sewer Network | SJ2761089840 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | n/a | n/a | Commissioned in 2017 - full year data expected | 1.13 | 3 | 100%
United Utilities | BRISCOE LANE CSO | Briscoe Lane CSO | 016982735 | MAN0337 | SO | CSO on Sewer Network | SJ8747099340 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 5.38 | 6 | 99.96%
United Utilities | BROADBOTTOM PUMPING STATION | Broadbottom PS | 016940167 | TAM0147 | SO | Storm Discharge at Pumping Station | SJ9871093160 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | n/a | n/a | Commissioned in 2018 - full year data expected | 3.87 | 25 | 100%
United Utilities | BROADHEAD ROAD CSO 051FX | BROADHEAD ROAD CSO | 01BBN0019 | BBN0019 | SO | CSO on Sewer Network | SD7433016820 | GB112069064580 | Bradshaw Brook | TRIB QUARLTON BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 37.57 | 22 | 90.97%
United Utilities | BROADOAK/LYDHURST AVE | Broadoak/Lyndhurst Avenue CSO | 01TAM0047 | TAM0047 | SO | CSO on Sewer Network | SD9395000310 | GB112069061151 | Medlock (Source to Lumb Brook) | TAUNTON (SMALLSHAW BECK) | N/A | N/A | Commissioned in 2019 - full year data expected | 209.35 | 68 | 59.74% | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BROMBOROUGH POOL VILLAGE PS 51026 | Bromborough Pool Village PS | 016881615 | WIR0133 | SO | Storm Discharge at Pumping Station | SJ3541084411 | 171 | #N/A | MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 44.07 | 6 | 99.94%
United Utilities | BROMBOROUGH WWTW | BROMBOROUGH WwTW | 016993398 | 16993398 | ST | Storm Tank at WwTW | SJ3471085640 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 2496.73 | 149 | 99.2% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BROMBOROUGH WWTW | BROMBOROUGH WwTW | 016993398 | 16993398 | SO | Inlet CSO at WwTW | SJ3471085640 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 1568.52 | 148 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BROMFIELD WWTW | BROMFIELD WwTW | 017570013 | 17570013 | SO | Inlet CSO at WwTW | NY1802047230 | GB102075073480 | Crummock Beck u/s Holme Dub | CRUMMOCK BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 287.43 | 21 | 100%
United Utilities | BROMLEY RD CORONATION RD CSO 131GZ | BROMLEY ROAD / CORONATION ROAD CSO | 01CON0031 | CON0031 | SO | CSO on Sewer Network | SJ8638063260 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA SWS | N/A | N/A | Commissioned in 2018 - full year data expected | 17.63 | 45 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BROMLEY ROAD CSO | Bromley Road CSO | 016892195 | CON0038 | SO | CSO on Sewer Network | SJ8670063170 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 2.43 | 12 | 82.89% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | BROMLEY STREET CSO 281MT | Bromley Street Nr Railway Arch CSO | 016982627 | MAN0310 | SO | CSO on Sewer Network | SJ8449099400 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 2.83 | 16 | 100%
United Utilities | BROOK CLOSE CSO | Wellington Road CSO | 016940411 | TRA0072 | SO | CSO on Sewer Network | SJ7720089290 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | n/a | n/a | Commissioned in 2018 - full year data expected | 139.9 | 40 | 99.6% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BROOK CORNER CSO | Brook Corner CSO | 01FYL0015 | FYL0015 | SO | CSO on Sewer Network | SD3970027701 | 176 | #N/A | RIVER RIBBLE | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | BROOK DEANS CLOSE CSO | Brook Dean Close (Smithhills Dean Road) Combined Sewer Overflow | 016982822 | BOL0179 | SO | CSO on Sewer Network | SD7003011330 | GB112069064560 | Astley Brook (Irwell) | DEAN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 29.1 | 15 | 49.98% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | BROOK LANE PUMPING STATION | Brook Lane PS | 017091517 | CHR0033 | SO | Storm Discharge at Pumping Station | SD5492015780 | GB112070061600 | Smithy Brook | SMITHY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 268.09 | 39 | 100%
United Utilities | BROOK MILL COMBINED SEWER OVERFLOW | Brook Mill CSO | 016881909 | CON0043 | SO | CSO on Sewer Network | SJ7575060100 | GB112068055430 | Arclid Brook | CLVRTD SECTION OF BROOK MILL | N/A | N/A | Commissioned in 2019 - full year data expected | 8.53 | 13 | 100%
United Utilities | BROOKHOUSE GREEN WASTEWATER WORKS | BROOKHOUSE GREEN WwTW 1-6 MOSS MERE | 016892175 | 16892175 | SO | Inlet CSO at WwTW | SJ8055061340 | GB112068055430 | Arclid Brook | TRIBUTARY OF RIVER WHEELOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 46.02 | 9 | 100%
United Utilities | BROOKLANDS ROAD/TODMORDEN ROAD CSO | BROOKLANDS ROAD / TODMORDEN ROAD CSO | 01BUR0032 | BUR0032 | SO | CSO on Sewer Network | SD8476031310 | GB112071065060 | Calder - headwaters to conf Brun | UNNAMED TRIB OF RIVER CALDER | N/A | N/A | Commissioned in 2019 - full year data expected | 17.43 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BROOKSIDE CSO | Brookside CSO | 017580239 | COP0091 | SO | CSO on Sewer Network | NY0211013960 | GB112074070010 | Ehen (upper including Liza) | RIVER EHEN | N/A | N/A | Commissioned in 2020 - full year data expected | 408.93 | 79 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery
United Utilities | BROOMHALL SPS | Sandford Banks PS | 016810292 | CRE0024 | SO | Storm Discharge at Pumping Station | SJ6220047200 | GB112068055470 | Weaver (Marbury Brook to Barnett Brook) | TRIB RIVER WEAVER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BROOMSTAIR ROAD CSO | Broomstair Road CSO | 016982919 | TAM0171 | SO | CSO on Sewer Network | SJ9304096520 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 418.53 | 63 | 74.69% | Sensor failure / issue | Resolved - October | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BROUGH WWTW | BROUGH WwTW | 017670004 | 17670004 | ST | Storm Tank at WwTW | NY7892014180 | GB102076070650 | Swindale Beck Great Musgrave | SWINDALE BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 2779.63 | 164 | 99.8% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | BROUGH WWTW | BROUGH WwTW | 017670004 | 17670004 | SO | Inlet CSO at WwTW | NY7892014180 | GB102076070650 | Swindale Beck Great Musgrave | SWINDALE BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 309 | 114 | 99.8% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | BROUGHAM PUMPING STATION | Brougham Pumping Station (17502) (EDE0085) | 017680334 | EDE0085 | SO | Storm Discharge at Pumping Station | NY5317028700 | GB102076071010 | Lowther (Lower) | TRIB RIVER EAMONT | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.99%
United Utilities | BROWNEDGE LANE CSO 401GR | Brownedge Lane CSO | 017180538 | SRI0058 | SO | CSO on Sewer Network | SD5633026290 | GB112071065300 | Darwen - conf Roddlesworth to tidal | COCKSHOTT BK TRB R DARWEN | n/a | n/a | Commissioned in 2018 - full year data expected | 1.57 | 2 | 99.99%
United Utilities | BROWNHILL DRIVE CSO | BROWNHILL DRIVE CSO | 01BBN0013 | BBN0013 | SO | CSO on Sewer Network | SD6948029920 | GB112071065310 | Blakewater | TRIB OF RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 2.8 | 5 | 100%
United Utilities | BRYN ROAD | Bryn Road CSO | 01WIG0104 | WIG0104 | SO | CSO on Sewer Network | SJ5857098960 | GB112069061220 | Millingford (Newton) Brook | MILLINGFORD BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 35.34 | 50 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BUCKLEY WELLS CSO 091DG | Buckley Wells CSO | 01BRY0023 | BRY0023 | SO | CSO on Sewer Network | SD7947009840 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 156.4 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | BUCKTON VALE ROAD CSO | Buckton Vale Road CSO | 016993735 | TAM0093 | SO | CSO on Sewer Network | SD9768000050 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | A CULVERTED TRIB TO RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 0.37 | 1 | 92.42%
United Utilities | BUFFALO COURT DETENTION TANK | BUFFALO COURT DETENTION TANK (37066) | EPRDB3690DM | SAL0195 | SO | CSO on Sewer Network | SJ8013097730 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BULK ROAD CSO 25097 | Bulk Road CSO (25097) | 017280370 | LAN0018 | SO | CSO on Sewer Network | SD4799062091 | 178 | #N/A | RIVER LUNE EST (VIA MILL RACE) | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 26.83 | 13 | 100%
United Utilities | BULKELEY STW | BULKELEY WwTW | 016810057 | 16810057 | SO | Inlet CSO at WwTW | SJ5325055130 | GB112068055300 | Weaver (Source to Marbury Brook) | TRIB RIVER WEAVER | n/a | n/a | Commissioned in 2018 - full year data expected | 444.07 | 54 | 99.76% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BULL BECK BROOKHOUSE CSO | Bull Beck Brookhouse Combined Sewer Overflow (Site ID 251HH) (LAN0089) | 017280284 | LAN0089 | SO | CSO on Sewer Network | SD5408064800 | GB112072065980 | Lune - conf Wenning to tidal | BULL BECK | Lune (Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 69.13 | 13 | 100%
United Utilities | BULLGILL WASTEWATER TREATMENT WORKS | BULLGILL WwTW | 017570067 | 17570067 | SO | Inlet CSO at WwTW | NY0972038620 | GB112075073640 | Ellen (lower) | RIVER ELLEN | Silloth | Allonby | Commissioned in 2017 - full year data expected | 113.49 | 67 | 99.71% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | BUNBURY STW | BUNBURY WwTW | 016810027 | 16810027 | SO | Inlet CSO at WwTW | SJ5733058130 | GB112068060280 | Gowy and tribs (Source to Milton Brook) | RIVER GOWY | N/A | N/A | Commissioned in 2020 - full year data expected | 120.42 | 59 | 99.99% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - October
United Utilities | BURGH-BY-SANDS WWTW | BURGH BY SANDS WwTW | 017670208 | 17670208 | SO | Inlet CSO at WwTW | NY3185059230 | 89 | #N/A | TRIB RIDDING SOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 185.94 | 36 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | BURNLEY RD E/BOOTH ST CSO | Burnley Road East/Booth Street CSO | 01ROS0041 | ROS0041 | SO | CSO on Sewer Network | SD8339021940 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.4 | 5 | 100%
United Utilities | BURNLEY RD/MIDDLEGATE CSO | Burnley Road/Middlegate CSO | 016982931 | ROS0078 | SO | CSO on Sewer Network | SD8095026100 | GB112069064680 | Limy Water | LIMY WATER TRIB OF IRWELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BURNLEY ROAD BACUP CSO | BURNLEY ROAD (BACUP) CSO | 01ROS0034 | ROS0034 | SO | CSO on Sewer Network | SD8668023570 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 5.67 | 6 | 100%
United Utilities | BURNLEY ROAD CSO 099BL | BURNLEY ROAD CSO | 01BRY0006 | BRY0006 | SO | CSO on Sewer Network | SD8041013840 | GB112069064620 | Irwell (Rossendale STW to Roch) | WALMERSLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 95.93 | 69 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BURNLEY ROAD EAST/SHAWCLOUGH CSO | Burnley Road East/Shawclough Road CSO | 01ROS0027 | ROS0027 | SO | CSO on Sewer Network | SD8362023210 | GB112069064670 | Whitewell Brook | WHITEWLL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.47 | 2 | 100%
United Utilities | BURNLEY ROAD EAST/TOWNLEY ARMS CSO | Burnley Road East/Townley Arms CSO | 016993545 | ROS0029 | SO | CSO on Sewer Network | SD8392025240 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 4.57 | 38 | 100%
United Utilities | BURNLEY ROAD EAST/TOWNLEY ARMS CSO | Burnley Road East/Whitewall Bottom CSO | 016993545 | ROS0028 | SO | CSO on Sewer Network | SD8392025240 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.7 | 1 | 100%
United Utilities | BURNLEY STW | BURNLEY WwTW | 017160005 | 17160005 | ST | Storm Tank at WwTW | SD8285035120 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER (RIBBLE) | N/A | N/A | Commissioned in 2019 - full year data expected | 2002.03 | 131 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BURSCOUGH WWTW | BURSCOUGH WwTW | 017030001 | 17030001 | ST | Storm Tank at WwTW | SD4249013290 | GB112070064880 | Back Drain and Sluice | BOATHOUSE SLUICE | n/a | n/a | Commissioned in 2018 - full year data expected | 292.78 | 21 | 100%
United Utilities | BURTON ROAD WITHINGTON CSO 28056 | Burton Road (Withington) CSO | 01MAN0237 | MAN0237 | SO | CSO on Sewer Network | SJ8346091621 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 1.23 | 6 | 100%
United Utilities | BURTON ST NR DALTON ST CSO 281HX | Burton Street near Dalton Street CSO | 016982622 | MAN0263 | SO | CSO on Sewer Network | SJ8486099630 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 30.47 | 22 | 100%
United Utilities | BURTON-IN-LONSDALE STW | BURTON-IN-LONSDALE WwTW | 017260021 | 17260021 | ST | Storm Tank at WwTW | SD6495271922 | GB112072071610 | Greta | RIVER GRETA | N/A | N/A | Commissioned in 2020 - full year data expected | 550.25 | 153 | 100% |  |  | Performance - Pump failure / issue
United Utilities | BURY NEW ROAD CSO | Bury New Road CSO | 016982878 | BRY0131 | SO | CSO on Sewer Network | SD8206002330 | GB112069061451 | Irwell (Croal to Irk) | SINGLETON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | BURY NEW ROAD CSO | Bury New Road CSO | 016982878 | BRY0130 | SO | CSO on Sewer Network | SD8206002330 | GB112069061451 | Irwell (Croal to Irk) | SINGLETON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 147.03 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BURY NEW ROAD SALFORD CSO | Ashworth Street CSO | 016993784 | SAL0024 | SO | CSO on Sewer Network | SJ8308399365 | GB112069061451 | Irwell (Croal to Irk) | THE RIVER IRWELL VIA SWS | N/A | N/A | Commissioned in 2018 - full year data expected | 32.52 | 43 | 46.88% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | BURY NEW ROAD SALFORD CSO | Bury New Road/Lockett Street CSO | 016993784 | MAN0393 | SO | CSO on Sewer Network | SJ8308399365 | GB112069061451 | Irwell (Croal to Irk) | THE RIVER IRWELL VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 23.2 | 15 | 100%
United Utilities | BURY NEW ROAD/WATERLOO ROAD CSO | Bury New Road/Waterloo Road CSO | 016982984 | MAN0360 | SO | CSO on Sewer Network | SJ8349099550 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 143.17 | 22 | 99.99%
United Utilities | BURY WASTEWATER TREATMENT WORKS | BURY WwTW | 016950033 | 16950033 | ST | Storm Tank at WwTW | SD8004007810 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 4: No cost beneficial solution | Investigation now complete, remedial work due
United Utilities | BURY WASTEWATER TREATMENT WORKS | BURY WwTW | 016950033 | 16950033 | SO | Inlet CSO at WwTW | SD8004007810 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | BUTLER STREET/WOODWARD STREET CSO | Butler Street/Woodward Street CSO | 01MAN0038 | MAN0038 | SO | CSO on Sewer Network | SJ8558095740 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER MEDLOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 2.5 | 16 | 100%
United Utilities | BUXTON RD ANDREW LN CSO 435GX | Buxton Road/Andrew Lane CSO | 01STK0093 | STK0093 | SO | CSO on Sewer Network | SJ9556085430 | GB112069060950 | Poise Brook | UNNAMED BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 1062.03 | 165 | 90.6% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CABLE STREET CSO 251H9 | Cable Street Combined Sewer Overflow (Site ID 251H9) (LAN0020) | 017280369 | LAN0020 | SO | CSO on Sewer Network | SD4761061941 | 178 | #N/A | LUNE ESTUARY | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 37.65 | 26 | 100%
United Utilities | CAIRD AVENUE COMBINED SEWEROVERFLOW | Caird Avenue CSO | 017680416 | CAR0001 | SO | CSO on Sewer Network | NY3855057430 | GB102076073940 | Eden - Eamont to tidal | POW BECK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | CALDBECK WWTW | CALDBECK WwTW | 017670113 | 17670113 | ST | Storm Tank at WwTW | NY3289039920 | GB102076073740 | Whelpo (Cald) Beck | CALD BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 861.4 | 80 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | CALDER BRIDGE WWTW | CALDER BRIDGE WwTW | 017470034 | 17470034 | ST | Storm Tank at WwTW | NY0367004920 | GB112074069730 | Calder (Lower) | RIVER CALDER | N/A | Seascale | Commissioned in 2016 - full year data expected | 679.59 | 149 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CALDER VALE PUMPING STATION | Calder Vale PS | 017290476 | WYR0078 | SO | Storm Discharge at Pumping Station | SD5311045170 | GB112072066220 | Calder (Wyre) | RIVER CALDER | Lune (Wyre) | Fleetwood | Commissioned in 2017 - full year data expected | 52.54 | 17 | 99.97%
United Utilities | CALDER, HUNCOAT INDUSTRIAL ESTATE | Huncoat Industrial Site | 01HYN0012 | HYN0012 | SO | CSO on Sewer Network | SD7730130446 | GB112071065490 | Calder - Pendle Water to conf Ribble | CLOUGH BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CALEDONIA ST HIBERNIA ST CSO 071IB | Caledonia Street/Hibernia Street CSO | 016982882 | BOL0231 | SO | CSO on Sewer Network | SD7080009120 | GB112069064540 | Middle Brook | MIDDLE BROOK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 94.37%
United Utilities | CALF HALL ROAD CSO | Calf Hall Road CSO | 017190815 | PEN0024 | SO | CSO on Sewer Network | SD8746046640 | GB112071065540 | Stock Beck | CALF HALL BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 2 | 5 | 99.98%
United Utilities | CAMBRIDGE STREET CSO 282D9 | Cambridge Street CSO | 016982721 | MAN0285 | SO | CSO on Sewer Network | SJ8385097410 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | CAMERTON WW PUMPING STATION | Camerton Ww PS | 017580269 | ALL0118 | SO | Storm Discharge at Pumping Station | NY0380030550 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 385.7 | 48 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CAMERTON WWTW CAMER | CAMERTON WwTW | 017570030 | 17570030 | ST | Storm Tank at WwTW | NY0298030100 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 2.07 | 2 | 99.97%
United Utilities | CAMMERCLOUGH ROAD CSO | Clammerclough CSO | 016993549 | BOL0147 | SO | CSO on Sewer Network | SD7473006060 | GB112069061451 | Irwell (Croal to Irk) | RIVER CROAL | n/a | n/a | Commissioned in 2018 - full year data expected | 476.51 | 117 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CANAL BANK TRANSFORMER HSE CSO | Canal Bank near Transformer House CSO | 01TAM0122 | TAM0122 | SO | CSO on Sewer Network | SJ9752099910 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | SWINESHAW BROOK TRIB RVR TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 78.07 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CANN BRIDGE STREET CSO 40042 | Cann Bridge Street CSO | 017160142 | SRI0008 | SO | CSO on Sewer Network | SD5758027610 | GB112071065300 | Darwen - conf Roddlesworth to tidal | RIVER DARWEN | n/a | n/a | Commissioned in 2018 - full year data expected | 191.73 | 94 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CARGO WASTEWATER TREATMENT WORKS | CARGO WwTW | 017670194 | 17670194 | SO | Inlet CSO at WwTW | NY3610058800 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | Solway | n/a | Commissioned in 2017 - full year data expected | 3503.37 | 361 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | CARK TANK NO.1 PUMPINT STATION | Cark PS | 01LAK0076 | LAK0076 | SO | Storm Discharge at Pumping Station | SD3578076410 | GB112073071270 | Eea | RIVER EEA | MORECAMBE BAY (LEVEN) | N/A | Commissioned in 2018 - full year data expected | 1363.03 | 88 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CARLETON HALL TEMPLEBANK CSO | Carleton Hall Templebank CSO | NPSWQD002845 | EDE0116 | SO | CSO on Sewer Network | NY5306029380 | GB102076071020 | Eamont (Upper) | UNNAMED CULVERT OF EAMONTRIVER | n/a | n/a | Commissioned in 2018 - full year data expected | 743.58 | 94 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | CARLETON MILL PUMPING STATION | Carleton Mill Pumping Station (10018) (CAR0074) | 017680319 | CAR0074 | SO | Storm Discharge at Pumping Station | NY4290052560 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | n/a | n/a | Commissioned in 2018 - full year data expected | 225.83 | 39 | 99.89%
United Utilities | CARLISLE WWTW | CARLISLE WwTW | 017670049 | 17670049 | ST | Storm Tank at WwTW | NY3847056520 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | Solway | N/A | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | CARLISLE WWTW | CARLISLE WwTW | 017670049 | 17670049 | SO | Inlet CSO at WwTW | NY3847056520 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | Solway | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | CARR CLOUGH CSO 091IG | Carr Clough CSO | 01BRY0044 | BRY0044 | SO | CSO on Sewer Network | SD8034002600 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH CLVRT IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 55.77 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CARR MILL ROAD CSO | Carr Mill Road CSO | 016982538 | STH0059 | SO | CSO on Sewer Network | SJ5290097558 | GB112069061230 | Black Brook (Mersey Estuary) | BLACK BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 195.65 | 80 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CARR MILL STREET CSO | Carr Mill Street/Hud Hey Road CSO | 016993764 | ROS0035 | SO | CSO on Sewer Network | SD7858024380 | GB112069064650 | Ogden | CLVRT'D SECTION SWINNEL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 306.85 | 69 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CARR STREET CSO 099BP | CARR STREET CSO | 01BRY0001 | BRY0001 | SO | CSO on Sewer Network | SD7935016470 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 2.33 | 16 | 100%
United Utilities | CARR WOOD COMBINED SEWER OVERFLOW | Carr Wood CSO | 016982756 | STK0051 | SO | CSO on Sewer Network | SJ8898085860 | GB112069060940 | Micker Brook | CARR BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 214.6 | 30 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CARRINGTON LANE | Carrington Road Bridge CSO | 016993623 | TRA0001 | SO | CSO on Sewer Network | SJ7420093770 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2020 - full year data expected | 14.13 | 10 | 100%
United Utilities | CARRINGTON RD | Carrington Road PS | 01TRA0024 | TRA0024 | SO | Storm Discharge at Pumping Station | SJ7439093820 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2019 - full year data expected | 320.6 | 65 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CARRINGTON RD/OFFERTON ST | Carrington Road/Offerton Street CSO | 016982686 | STK0132 | SO | CSO on Sewer Network | SJ9067090960 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CART LANE PUMPING STATION | Cart Lane (Grange) PS | 017370129 | LAK0073 | SO | Storm Discharge at Pumping Station | SD4027076810 | 184 | #N/A | KENT CHANNEL | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 370.72 | 25 | 99.69%
United Utilities | CARTMEL CLOSE CSO | Cartmel Close (Macclesfield) Combined Sewer Overflow (Site ID 273BV) (MAC0061) | 016892095 | MAC0061 | SO | CSO on Sewer Network | SJ9082075120 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Commissioned in 2019 - full year data expected | 288.77 | 49 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CARTMEL IN CARK PUMPING STATION | Cartmel In Cark Pumping Station (Site ID CARTC) (LAK0099) | 017380400 | LAK0099 | SO | Storm Discharge at Pumping Station | SD3651076350 | GB112073071270 | Eea | RIVER EEA | Morecambe Bay (Leven) | n/a | Commissioned in 2018 - full year data expected | 4701.64 | 314 | 98.26% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CASTERTON WWTW | CASTERTON WwTW | 017270014 | 17270014 | ST | Storm Tank at WwTW | SD6176079550 | GB112072071690 | Lune - conf Rawthey to conf Greta | RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 52.8 | 9 | 99.95%
United Utilities | CASTLE CARROCK WWTW | CASTLE CARROCK WwTW | 017670090 | 17670090 | SO | Inlet CSO at WwTW | NY5409055900 | GB102076074040 | Gelt | CASTLE CARROCK BECK | n/a | n/a | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | CASTLE CARROK CSO | Castle Carrok CSO (Adjacent Donlea House) | 017680315 | CAR0069 | SO | CSO on Sewer Network | NY5422055720 | GB102076074040 | Gelt | CASTLE CARROCK BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 8.77 | 11 | 100%
United Utilities | CASTLE DRIVE CSO | Castle Hill Drive CSO | 01EDE0035 | EDE0035 | SO | CSO on Sewer Network | NY5188029731 | GB102076071020 | Eamont (Upper) | DOG BECK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 83.33% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | CASTLE INN ROAD MOSSLEY CSO | Castle Inn Road (Mossley) Combined Sewer Overflow (Site ID 13531) (CON0034) | 016892193 | CON0034 | SO | CSO on Sewer Network | SJ8833061430 | GB112068055360 | Biddulph Brook | TRIB OF DANE-IN-SHAW BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 5.7 | 4 | 100%
United Utilities | CASTLE ST | Castle Street, Northwich | 01VRY0103 | VRY0103 | SO | CSO on Sewer Network | SJ6567073680 | GB112068060460 | Weaver (Marbury Brook to Dane) | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CASTLETON AVENUE CSO 451IU | Castleton Avenue CSO | 016940192 | TRA0065 | SO | CSO on Sewer Network | SJ7878095380 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK TRIB SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 1.7 | 4 | 100%
United Utilities | CASTLETON SOUTH JUNCTION CSO | Adj M62 Castleton | 01ROC0094 | ROC0094 | SO | CSO on Sewer Network | SD8814009780 | GB112069061161 | Irk (Sourtce to Wince Brook) | 0 | N/A | N/A | Commissioned in 2019 - full year data expected | 167.23 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CASTLETON WWTW CSTLT | CASTLETON WwTW | 016950034 | 16950034 | ST | Storm Tank at WwTW | SD8803009580 | GB112069061161 | Irk (Sourtce to Wince Brook) | TRUB BROOK TRIB RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 1082.09 | 90 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CATON WASTEWATER TREATMENT WORKS | CATON WwTW | 017270001 | 17270001 | ST | Storm Tank at WwTW | SD5277065250 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 0 | 0 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CATTERALL LANE WTP | A6 Junction of Churchtown CSO | 017260074 | WYR0031 | SO | CSO on Sewer Network | SD4570041150 | GB112072066250 | Wyre - conf R Brock to tidal | TIDAL RIVER WYRE | N/A | N/A | Commissioned in 2020 - full year data expected | 220.83 | 87 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CATTLE MARKET CSO | Cattle Market CSO | 017180626 | PRE0065 | SO | CSO on Sewer Network | SD5279031260 | GB112071065470 | Savick Brook | EAVES BK, TRIB OF SAVICK BK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CAUSEWAY PS | Causeway Pumping Station | 01WAR0005 | WAR0005 | SO | Storm Discharge at Pumping Station | SJ6068087600 | GB531206908100 | MERSEY | 0 | N/A | N/A | Commissioned in 2020 - full year data expected | 1.26 | 4 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | CAUSEY WAY COMBINED SEWER OVERFLOW | Causey Way CSO | 017190839 | SRI0030 | SO | CSO on Sewer Network | SD5404026650 | 175 | #N/A | BOUNDARY BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 177.97 | 64 | 99.85% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CECIL ROAD/ASHLEY ROAD CSO | Cecil Road/Ashley Road CSO | 01TRA0012 | TRA0012 | SO | CSO on Sewer Network | SJ7682085960 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | TRIB OF RIVER BOLLIN VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | CEMETERY LANE PUMPING STATION | Cemetery Lane Pumping Station (52540) and Bridge Farm Combined Sewer Overflow (525QK) | EPRKB3498EP | WYR0040 | SO | Storm Discharge at Pumping Station | SD3707046030 | GB112069061451 | Irwell (Croal to Irk) | UNKNOWN | N/A | N/A | Commissioned in 2018 - full year data expected | 130.4 | 30 | 67.27% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | CENTRAL AVENUE CSO | Central Avenue CSO | 01MAN0008 | MAN0008 | SO | CSO on Sewer Network | SD8541001790 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2018 - full year data expected | 1.53 | 8 | 100%
United Utilities | CENTRAL PARK CSO 50090 | Central Park CSO | 01WIG0174 | WIG0174 | SO | CSO on Sewer Network | SD5875006330 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 528.82 | 129 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CENTRAL PUMPING STATION | Central Pumping Station | 01WIG0100 | WIG0100 | SO | Storm Discharge at Pumping Station | SD6689000000 | GB112069060810 | Bedford Brook | BEDFORD BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 8.74 | 33 | 99.99%
United Utilities | CHAIN BAR LANE CSO | Chain Bar Lane CSO | 016993552 | TAM0140 | SO | CSO on Sewer Network | SJ9869094790 | GB112069061050 | Etherow (Glossop Brook to Goyt) | HURST CLOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.84 | 5 | 99.98%
United Utilities | CHAIN LANE PUMPING STATION 19046 | Chain Lane PS | 01FYL0040 | FYL0040 | SO | Storm Discharge at Pumping Station | SD3563035590 | GB112072066120 | Hillylaid Pool - Tidal Wyre | TRIB OF WYRE | LUNE (WYRE ESTUARY) | Blackpool North | Commissioned in 2016 - full year data expected | 99.04 | 41 | 99.89% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHANCEL LANE CSO 271I4 | CHANCEL LANE CSO | 01MAC0046 | MAC0046 | SO | CSO on Sewer Network | SJ8481081550 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Commissioned in 2018 - full year data expected | 102.03 | 51 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CHAPEL GREEN ROAD | Junction of Romford Street & Chapel Green Road CSO | 01WIG0058 | WIG0058 | SO | CSO on Sewer Network | SD6196004410 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHAPEL GREEN ROAD/BRIDGEWATER ST | Chapel Green Road/Bridgewater Street CSO | 01WIG0060 | WIG0060 | SO | CSO on Sewer Network | SD6199004420 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHAPEL GREEN ROAD/ROMFORD ST CSO | Chapel Green Road/Romford Street CSO | 016993521 | WIG0057 | SO | CSO on Sewer Network | SD6196004412 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 71.9 | 52 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHAPEL HOUSE ROAD (32014) CSO | Chapel House Road CSO(32014) (PEN0084) | 017180623 | PEN0084 | SO | CSO on Sewer Network | SD8646037550 | GB112071065130 | Walverden Water | WALVERDEN WATER | n/a | n/a | Commissioned in 2018 - full year data expected | 59.64 | 37 | 99.99%
United Utilities | CHAPEL HOUSE ROAD CSO (32014) | Chapel House Road CSO | 01PEN0017 | PEN0017 | SO | CSO on Sewer Network | SD8646037540 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Commissioned in 2018 - full year data expected | 4127.5 | 281 | 99.86% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHAPEL LANE | Chapel Lane CSO | 01TRA0016 | TRA0016 | SO | CSO on Sewer Network | SJ7919085550 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHAPEL ST (TEMPLE SOWERBY) CSO | Chapel Street (Temple Sowerby) CSO | 01EDE0013 | EDE0013 | SO | CSO on Sewer Network | NY6175027321 | GB102076070950 | Crowdundle Beck - Lower | BIRK SIKE | N/A | N/A | Commissioned in 2019 - full year data expected | 41.07 | 29 | 100%
United Utilities | CHAPEL-EN-LE-FRITH WWTW | CHAPEL-EN-LE-FRITH WwTW | 016940168 | 16940168 | ST | Storm Tank at WwTW | SK0481082020 | GB112069060910 | Black Brook (Upper Mersey) | BLACK BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | Investigation now complete, remedial work due
United Utilities | CHAPELGREEN/ARUNDEL ST | Chapel Green Road/ Arundle Street CSO | 01WIG0059 | WIG0059 | SO | CSO on Sewer Network | SD6196004411 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHAPPELL ROAD CSO | Chappell Road CSO | 016983267 | TAM0006 | SO | CSO on Sewer Network | SJ9045799436 | GB112069061151 | Medlock (Source to Lumb Brook) | LUMB BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 163.04 | 63 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHARLES ST PRINCESS ST CSO 28116 | Charles Street/Princess Street CSO | 01MAN0166 | MAN0166 | SO | CSO on Sewer Network | SJ8433097510 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 2.53 | 10 | 100%
United Utilities | CHARLES STREET CSO | Charles Street CSO | 01MAN0183 | MAN0183 | SO | CSO on Sewer Network | SJ8432097500 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 1.03 | 2 | 100%
United Utilities | CHARLESTOWN ROAD CSO | Charlestown Road CSO | NPSWQD006371 | MAN0406 | SO | CSO on Sewer Network | SD8690103015 | GB112069061131 | Irk (Wince to Irwell) | BOGGART HOLE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 531.27 | 104 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHARLESWORTH PUMPING STATION | Charlesworth PS | 016892056 | PEA0091 | SO | Storm Discharge at Pumping Station | SJ9975093350 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Commissioned in 2019 - full year data expected | 200.54 | 26 | 99.97%
United Utilities | CHATBURN PUMPING STATION | Chatburn (Ribble Lane) PS | NPSWQD005629 | RIB0051 | SO | Storm Discharge at Pumping Station | SD7678044720 | GB112071065612 | Ribble DS Stock Beck | CHATBURN BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1146.12 | 114 | 98.88% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHATSWORTH AVENUE SPS | Chatsworth Avenue PS | 017260171 | BPL0038 | SO | Storm Discharge at Pumping Station | SD3116046680 | 349 | #N/A | IRISH SEA | Lune (Wyre Estuary) and Lune (Broadfleet and Plover Scar) | Bispham, Cleveleys, Fleetwood | Commissioned in 2017 - full year data expected | 111.19 | 35 | 99.94%
United Utilities | CHEADLE GOLF COURSE CSO (43198) | Cheadle Golf Course CSO | 016940447 | STK0049 | SO | CSO on Sewer Network | SJ8623087880 | GB112069060940 | Micker Brook | MICKER BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 202.74 | 55 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHEETHAM HILL ROAD CSO | Cheetham Hill Road CSO | 01TAM0078 | TAM0078 | SO | CSO on Sewer Network | SJ9489096610 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | JOHNSON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHERRY TREE WORKS SITE | Cherry Tree/Feniscowles CSO | 017190595 | BBN0083 | SO | CSO on Sewer Network | SD6590026282 | GB112071065250 | Roddlesworth | TRIB RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 3.23 | 5 | 92.49%
United Utilities | CHESTER ROAD/GREAT JACKSON ROAD CSO | Chester Road/Great Jackson Road CSO | 016982719 | MAN0276 | SO | CSO on Sewer Network | SJ8336097430 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 66.25 | 14 | 100%
United Utilities | CHESTER STREET CSO | Chester Street CSO | 016983278 | MAN0400 | SO | CSO on Sewer Network | SJ8408097350 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 1.25 | 2 | 100%
United Utilities | CHESTER WAY | Northwich Resewerage Scheme | 01VRY0001 | VRY0001 | SO | CSO on Sewer Network | SJ6593773780 | GB112068060470 | Dane (Wheelock to Weaver) | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHESTERGATE CSO 431A3 | Chestergate CSO | 01STK0110 | STK0110 | SO | CSO on Sewer Network | SJ8926090300 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2017 - full year data expected | 173.3 | 26 | 100%
United Utilities | CHESTERGATE/KING STREET WEST CSO | Chestergate/King Street West CSO | 016982674 | STK0111 | SO | CSO on Sewer Network | SJ8899090260 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 16.27 | 11 | 100%
United Utilities | CHESTNUT AVENUE PS | Chestnut Avenue PS | 016881932 | CON0086 | SO | Storm Discharge at Pumping Station | SJ8030057470 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | TRENT & MERSEY CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 49.7 | 33 | 100%
United Utilities | CHESTNUT ROAD CSO | Chestnut Road CSO | 01WIG0013 | WIG0013 | SO | CSO on Sewer Network | SD5877006571 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 5.37 | 17 | 100%
United Utilities | CHILTERN AVENUE CSO | Chiltern Avenue CSO | 017280299 | WYR0062 | SO | CSO on Sewer Network | SD3414039350 | 180 | #N/A | HORSE BRIDGE DYKE | LUNE (WYRE ESTUARY) | Fleetwood | Commissioned in 2016 - full year data expected | 0.83 | 4 | 100%
United Utilities | CHISWORTH MARPLE ROAD WWNPS | Chisworth (Marple Rd) WasteWater Network PS | 016982818 | PEA0071 | SO | Storm Discharge at Pumping Station | SK0003092290 | GB112069061050 | Etherow (Glossop Brook to Goyt) | CHISWORTH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 566.53 | 83 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CHORLEY LOWER WORKS PS | Chorley Lower Works PS | 017081342 | CHR0091 | SO | Storm Discharge at Pumping Station | SD5638017460 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | N/A | N/A | Commissioned in 2020 - full year data expected | 432.83 | 67 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHORLEY NEW RD TELFORD ST CSO 071JQ | CHORLEY NEW ROAD / TELFORD STREET CSO | 01BOL0133 | BOL0133 | SO | CSO on Sewer Network | SD6440010670 | GB112070064850 | Douglas - Upper | MIDDLE BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 2.27 | 6 | 100%
United Utilities | CHORLEY NEW ROAD CSO 071JS | CHORLEY NEW ROAD CSO | 01BOL0097 | BOL0097 | SO | CSO on Sewer Network | SD6874009330 | GB112069064540 | Middle Brook | TRIB OF MIDDLE BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 51.3 | 52 | 97.66% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CHORLEY NEW ROAD SPS | Chorley New Road/Beaumont Road CSO | 016982073 | BOL0096 | SO | CSO on Sewer Network | SD6440010671 | GB112070064850 | Douglas - Upper | PEARL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 169.7 | 80 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CHORLEY NEW/DEVONSHIRE ROAD CSO | CHORLEY NEW ROAD / DEVONSHIRE ROAD CSO | 01BOL0098 | BOL0098 | SO | CSO on Sewer Network | SD6964009300 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHORLEY OLD ROAD SPS | Chorley Old Road/Chorley New Road CSO | 016982075 | BOL0181 | SO | CSO on Sewer Network | SD6819010730 | GB112069064540 | Middle Brook | ASTLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 250.37 | 94 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CHORLEY RD, M.H. E36 | Chorley Road M.H E36 Standish | 01LA1617 | WIG0167 | SO | CSO on Sewer Network | SD5800009280 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS | N/A | N/A | Commissioned in 2020 - full year data expected | 162.83 | 57 | 99.73% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHORLEY WASTE WATER TREATMENT WORKS | Chorley WwTW | 017060016 | 17060016 | ST | Storm Tank at WwTW | SD5638217462 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW & CHOR | Ribble | St Annes St Annes North Southport Blackpool South | Commissioned in 2020 - full year data expected | 1684.72 | 87 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHORLTON STREET CSO 281J2 | CHORLTON STREET CSO | 01MAN0162 | MAN0162 | SO | CSO on Sewer Network | SJ8451097820 | GB112069061152 | Medlock (Lumb Brook to Irwell) | SHOOTERS BROOK TRIB RVR MEDLOC | N/A | N/A | Commissioned in 2018 - full year data expected | 10 | 18 | 100%
United Utilities | CHUDDLEIGH ROAD CSO | Chudleigh Road CSO | 016993672 | MAN0140 | SO | CSO on Sewer Network | SD8455002830 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 118.17 | 30 | 99.88%
United Utilities | CHURCH BANK (SIDE OF VIADUCT) CSO | Church Bank (Side of Viaduct) | 016982610 | BOL0184 | SO | CSO on Sewer Network | SD7214009260 | GB112069064540 | Middle Brook | CROAL MINOR | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | CHURCH BANK RAILWAY VIADUCT CSO | CHURCH BANK / RAILWAY VIADUCT CSO | 01BOL0130 | BOL0130 | SO | CSO on Sewer Network | SD7214009280 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Commissioned in 2017 - full year data expected | 1.33 | 8 | 100%
United Utilities | CHURCH LANE CREWE CSO | CHURCH LANE CSO (Crewe) | 01CRE0043 | CRE0043 | SO | CSO on Sewer Network | SJ6850054290 | GB112068055280 | Wistaston Brook | WISTATON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 436.28 | 86 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CHURCH ROAD | Urmston Sewerage, Church Road & Carrington Road PS | 01TRA0025 | TRA0025 | SO | Storm Discharge at Pumping Station | SJ7483093740 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHURCH ST | Church Street PS | 016892145 | VRY0045 | SO | Storm Discharge at Pumping Station | SJ6550066450 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CHURCH STREET CSO | Church Street CSO | 01VRY0104 | VRY0104 | SO | CSO on Sewer Network | SJ6631071100 | GB112068060470 | Dane (Wheelock to Weaver) | ELDERSBRIAR BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.13 | 1 | 100%
United Utilities | CHURCH STREET EAST 09003 | Church Street East CSO | 016993586 | BRY0031 | SO | CSO on Sewer Network | SD7909007251 | GB112069060840 | Irwell (Roch to Croal) | UNNAMED TRIB OF RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 278.24 | 24 | 99.77%
United Utilities | CHURCH STREET WEST CSO | Radclife Central CSO | 016993584 | BRY0128 | SO | CSO on Sewer Network | SD7662010460 | GB112069060840 | Irwell (Roch to Croal) | UNNAMED POND | n/a | n/a | Commissioned in 2018 - full year data expected | 69.88 | 31 | 99.95%
United Utilities | CHURCH STREET WEST CSO | Church Street West CSO | 016993584 | BRY0019 | SO | CSO on Sewer Network | SD7662010460 | GB112069060840 | Irwell (Roch to Croal) | UNNAMED POND | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | CHURCH STREET WEST CSO 091KB | Church Street West CSO | 01BRY0029 | BRY0029 | SO | CSO on Sewer Network | SD7878007090 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 1.3 | 3 | 100%
United Utilities | CHURCH STREET/PARLIAMENT STREET CSO | CHURCH STREET / PARLIAMENT STREEET CSO | 01BBN0122 | BBN0122 | SO | CSO on Sewer Network | SD6928022180 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | CULVERTED SECTION RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0.6 | 8 | 100%
United Utilities | CHURCH WHARFE CSO 073BW | CHURCH WHARF CSO | 01BOL0131 | BOL0131 | SO | CSO on Sewer Network | SD7215009280 | GB112069064540 | Middle Brook | CLVRT SEC RIVER CROAL MINOR | N/A | N/A | Commissioned in 2018 - full year data expected | 19.77 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CITY RD CSO 288OV | City Road CSO | 016982954 | MAN0366 | SO | CSO on Sewer Network | SJ8252097360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | VIA SWS MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 33.5 | 11 | 78.95% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | CITY WALK PS | Near City Walk | 016940402 | SAL0104 | SO | Storm Discharge at Pumping Station | SD7884002140 | GB112069061451 | Irwell (Croal to Irk) | TRIB SLACK BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 114.77 | 56 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLAPHAM WASTEWATER TREATMENT WORKS | Clapham WwTW | EPREP3526XK | EPREP3526XK | ST | Storm Tank at WwTW | SD7444068690 | GB112072071840 | Clapham Beck | RIVER WENNING | N/A | N/A | Commissioned in 2020 - full year data expected | 36.89 | 3 | 100%
United Utilities | CLARE RD/DAVENHILL RD CSO | Clare Road/Davenhill Road CSO | 016940833 | MAN0345 | SO | CSO on Sewer Network | SJ8735093540 | GB112069061410 | Fallowfield Brook | CRINGLE BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | CLARENCE STREET CSO | Clarence Street CSO | 017190797 | BBN0101 | SO | CSO on Sewer Network | SD6871023540 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 216.11 | 71 | 99.93% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CLAYTON BRIDGE | Clayton Bridge CSO | 01TAM0004 | TAM0004 | SO | CSO on Sewer Network | SJ8909099420 | GB112069061152 | Medlock (Lumb Brook to Irwell) | 0 | N/A | N/A | Commissioned in 2019 - full year data expected | 399.07 | 65 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLAYTON LE MOORS TANK CSO 22016 | Clayton-le-Moors Tank | 017160093 | HYN0004 | SO | CSO on Sewer Network | SD7428031740 | GB112071065070 | Hyndburn Brook - Lower | HYNDBURN BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 134.27 | 59 | 99.92% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CLEATOR WWTW | CLEATOR WwTW | 017470025 | 17470025 | ST | Storm Tank at WwTW | NY0129013190 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | n/a | Seascale | Commissioned in 2017 - full year data expected | 941.47 | 66 | 99.7% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLEATOR WWTW | CLEATOR WwTW | 017470025 | 17470025 | SO | Inlet CSO at WwTW | NY0129013190 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | N/A | N/A | Commissioned in 2017 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | CLEVELAND DRIVE CSO | Cleveland Drive CSO | 016983353 | WIG0106 | SO | CSO on Sewer Network | SJ5854499576 | GB112069061220 | Millingford (Newton) Brook | MILLINGFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 91.28 | 48 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLEVELAND RD DELAUNAY RD CSO 288NJ | Cleveland/Delauney's Road CSO | 01MAN0078 | MAN0078 | SO | CSO on Sewer Network | SD8505102790 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 44.73 | 50 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLEVELAND RD DELAUNEYS RD CSO 281KK | Cleveland Road/Delaunays CSO | 016993738 | MAN0117 | SO | CSO on Sewer Network | SD8500002810 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 3.43 | 11 | 100%
United Utilities | CLIFFORD AVENUE WW NTWK PS | Clifford Avenue CSO | 01SRI0041 | SRI0059 | SO | CSO on Sewer Network | SD4813026380 | 175 | #N/A | LONGTON BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 291.27 | 41 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLIFTON (PENRITH) PUMPING STATION | CLIFTON PS | NPSWQD009945 | EDE0118 | SO | Storm Discharge at Pumping Station | NY5300126548 | GB102076071010 | Lowther (Lower) | RIVER LOWTHER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CLIFTON HOLMES CSO | Clifton Holmes CSO | 016982526 | OLD0014 | SO | CSO on Sewer Network | SD9818008040 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 88.03 | 62 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLIFTON HOUSE ROAD PUMPING STATION | Clifton House Road (37010) (SAL0145) | 016940527 | SAL0145 | SO | Storm Discharge at Pumping Station | SD7698004370 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA S.W. | n/a | n/a | Commissioned in 2018 - full year data expected | 18.87 | 6 | 90.37%
United Utilities | CLIFTON PUMPING STATION | Clifton PS | 016940035 | SAL0148 | SO | Storm Discharge at Pumping Station | SD8004002540 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 469.16 | 76 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLIFTON PUMPING STATION | Clifton Village PS | 017091534 | PRE0121 | SO | Storm Discharge at Pumping Station | SD4679030010 | GB112071065670 | Dow Brook | SAVICK BROOK TRIBUTARY | n/a | n/a | Commissioned in 2018 - full year data expected | 66.56 | 39 | 99.94%
United Utilities | CLIFTON PUMPING STATION | Clifton PS | 017680335 | EDE0086 | SO | Storm Discharge at Pumping Station | NY5287027380 | GB102076071010 | Lowther (Lower) | TRIB RIVER LOWTHER | n/a | n/a | Commissioned in 2018 - full year data expected | 25.98 | 12 | 99.98%
United Utilities | CLIFTON RD LEACH ST CSO 091KQ | Clifton Road/Leach Street CSO | 01BRY0039 | BRY0039 | SO | CSO on Sewer Network | SD8056003980 | GB112069061451 | Irwell (Croal to Irk) | TRIB PRESTWICH CLOUGH VIA SWS | N/A | N/A | Commissioned in 2018 - full year data expected | 1.63 | 7 | 100%
United Utilities | CLITHEROE STREET CSO | Clitheroe Street CSO | 017160177 | RIB0030 | SO | CSO on Sewer Network | SD7330040560 | GB112071065510 | Mearley Brook | PENDLETON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 89.4 | 25 | 89.53%
United Utilities | CLITHEROE WWTW | CLITHEROE WwTW | 017160033 | 17160033 | ST | Storm Tank at WwTW | SD7262040390 | GB112071065510 | Mearley Brook | BARROW CLOUGH/PENDLETON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1510.85 | 104 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLOSE BROOK CSO | Close Brook CSO | 017091500 | WIG0168 | SO | CSO on Sewer Network | SD5636005900 | GB112070064820 | Douglas - Lower | CLOSE BROOK TRIB OF R DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 63.11 | 20 | 99.95%
United Utilities | CLOUGH END ROAD CSO 441KS | Clough End Road CSO | 01TAM0139 | TAM0139 | SO | CSO on Sewer Network | SJ9864094380 | GB112069061050 | Etherow (Glossop Brook to Goyt) | HURST CLOUGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 95.35%
United Utilities | CLOVER ROAD BUTTERWORTH BROW CSO | Clover Road/Butterworth Brow CSO | 01CHR0023 | CHR0023 | SO | CSO on Sewer Network | SD5683015940 | GB112070064952 | Yarrow DS Big Lodge Water | SWS TO RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 825.52 | 77 | 92.25% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLOVER ROAD PUMPING STATION | Clover Road PS | 017081574 | CHR0027 | SO | Storm Discharge at Pumping Station | SD5685015890 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 286.52 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CLOWES ST/DANIEL ADAMSON ROAD CSO | Clowes Street/Daniel Adamson Road CSO | 016993658 | SAL0073 | SO | CSO on Sewer Network | SJ7924097980 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 2019.87 | 142 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COALPIT WOOD CSO | Coal Pitt Wood CSO | 017580316 | ALL0019 | SO | CSO on Sewer Network | NY0915033110 | GB112075073570 | Broughton Beck | DOVENBY BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 93.5 | 32 | 100%
United Utilities | COCKERHAM CSO | Cockerham Adjacent to Manor Inn Car Park CSO | 017280280 | LAN0081 | SO | CSO on Sewer Network | SD4520051300 | 343 | #N/A | TRIB RIVER COCKER | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 2073.23 | 191 | 98.03% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COCKERMOUTH WWTW | COCKERMOUTH WwTW | 017570031 | 17570031 | ST | Storm Tank at WwTW | NY1024031140 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 2378.89 | 136 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COLLEGE ROAD ESHE ROAD CSO 38109 | College Road/Eshe Road | 016982755 | SEF0102 | SO | CSO on Sewer Network | SJ3149099470 | 348 | #N/A | RIVER MERSEY ESTUARY | N/A | N/A | Commissioned in 2016 - full year data expected | 84.23 | 44 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | COLLYHURST RD/BARNSTAPLE DRIVE CSO | Collyhurst Road/Barnstaple Drive CSO | 01MAN0054 | MAN0054 | SO | CSO on Sewer Network | SD8533000540 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | COLNE REFUSE TRANSFER STATION | Colne Refuse Transfer Station CSO (Site ID 322YC) (PEN0059) | 01PEN0059 | PEN0059 | SO | CSO on Sewer Network | SD8749039380 | GB112071065200 | Colne Water - Trawden Bk to Wanless Water | COLNE WATER | n/a | n/a | Commissioned in 2017 - full year data expected | 75.73 | 32 | 100%
United Utilities | COLNE WASTE WATER TREATMENT WORKS | Colne WwTW | 017160006 | 17160006 | ST | Storm Tank at WwTW | SD8703039470 | GB112071065200 | Colne Water - Trawden Bk to Wanless Water | COLNE WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 1707.11 | 126 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COMBERBACH PS | Comberbach PS | 016810065 | VRY0128 | SO | Storm Discharge at Pumping Station | SJ6499077140 | GB112068060400 | Forge (Kidd) Brook | KID (FORGE) BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 125.82 | 37 | 99.99%
United Utilities | COMMERCIAL BROW CSO | COMMERCIAL BROW CSO | 01TAM0081 | TAM0081 | SO | CSO on Sewer Network | SJ9554095390 | GB112069061280 | Wilson Brook | WILSON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | COMMERCIAL BROW CSO | Commercial Brow CSO | 016940359 | TAM0149 | SO | CSO on Sewer Network | SJ9524095190 | GB112069061280 | Wilson Brook | GODLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 22.49 | 21 | 100%
United Utilities | COMMON BANK LANE CSO CHORL | Common Bank Lane CSO | 017081355 | CHR0090 | SO | CSO on Sewer Network | SD5678017740 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER CHOR DIVERSION CHANNEL | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | COMMON END COMBINED SEWER OVERFLOW | Common End CSO | 017480427 | COP0003 | SO | CSO on Sewer Network | NY0043022740 | GB112074070040 | Lowca Beck | DISTINGTON BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | COMPSTALL RD (NEAR IRONBRIDGE) CSO | Compstall Road CSO | 01STK0052 | STK0052 | SO | CSO on Sewer Network | SJ9643090200 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Commissioned in 2016 - full year data expected | 131.97 | 30 | 100%
United Utilities | COMPSTALL ROAD CSO | Compstall Road (Romilly)CSO | 016982502 | STK0131 | SO | CSO on Sewer Network | SJ9643090690 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Commissioned in 2019 - full year data expected | 256.54 | 73 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COMPSTALL ROAD CSO | Compstall Road CSO | 016982502 | STK0139 | SO | CSO on Sewer Network | SJ9643090690 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | n/a | n/a | Commissioned in 2019 - full year data expected | 44.2 | 28 | 100%
United Utilities | CONGLETON STW | CONGLETON WwTW | 016810066 | 16810066 | SO | Inlet CSO at WwTW | SJ8538263482 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 99.89%
United Utilities | CONGLETON STW | CONGLETON WwTW | 016810066 | 16810066 | ST | Storm Tank at WwTW | SJ8538263482 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 96.66%
United Utilities | CONISTON WWTW | Coniston WwTW | 017370035 | 17370035 | ST | Storm Tank at WwTW | SD3072097050 | GB112073071210 | Yewdale/Church Beck | CHURCH BECK | N/A | N/A | Commissioned in 2016 - full year data expected | 2710.23 | 138 | 99.52% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | COOKESMERE LANE | Cooksmere Lane PS | 01CON0070 | CON0070 | SO | Storm Discharge at Pumping Station | SJ7502061790 | GB112068055460 | Croco | TRIB OF THE RIVER CROCO | n/a | n/a | Commissioned in 2018 - full year data expected | 72.5 | 16 | 99.92%
United Utilities | COOPER LANE SPS | Cooper Lane Pumping Station (Site ID 39056) (LAK0092) | 017280253 | LAK0092 | SO | Storm Discharge at Pumping Station | SD3085074800 | GB531207311900 | LEVEN | LEVEN ESTUARY | Morecambe Bay (Leven) | n/a | Commissioned in 2017 - full year data expected | 379.54 | 27 | 99.96%
United Utilities | COP LANE CSO | Cop Lane CSO | 017190853 | SRI0031 | SO | CSO on Sewer Network | SD5223028130 | 175 | #N/A | TRIBOF RIVER RIBBLE | n/a | n/a | Commissioned in 2018 - full year data expected | 19.33 | 4 | 99.96%
United Utilities | COPPICESIDE PS DISLEY | Coppiceside PS | 016940142 | MAC0159 | SO | Storm Discharge at Pumping Station | SJ9585084620 | GB112069060920 | Micker (Norbury) Brook | BOLLINHURST BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | COPPULL NEW RD/BUTTERWORTH RD CSO | Coppull New Road/Butterworth Brow CSO | 017081147 | CHR0050 | SO | CSO on Sewer Network | SD5685015931 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | N/A | N/A | Commissioned in 2017 - full year data expected | 426.23 | 105 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | COPSTER GREEN SEWER EJE | Copster Green Sewer Ejector Station | 01RIB0048 | RIB0048 | SO | Storm Discharge at Pumping Station | SD6745034230 | GB112071065710 | Showley Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CORFE CRESCENT CSO | Outside No.1 Corfe Crescent CSO | NPSWQD010100 | STK0150 | SO | CSO on Sewer Network | SJ9149086250 | GB112069060920 | Micker (Norbury) Brook | NORBURY BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.23 | 1 | 100%
United Utilities | CORNMILL BRIDGE CSO | Cornmill Bridge CSO | 016993523 | PEA0027 | SO | CSO on Sewer Network | SK0397094170 | GB112069060730 | Glossop (Shelf) Brook (Source to Long Clough Brook) | SHELF BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 497.57 | 94 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CORNMILL COTTAGES CSO | Cornmill Cottages CSO | 01PEN0021 | PEN0021 | SO | CSO on Sewer Network | SD8778047180 | GB112071065540 | Stock Beck | BUTTS BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.27 | 2 | 100%
United Utilities | CORPORATION STREET | Corporation Street CSO | 01TAM0099 | TAM0099 | SO | CSO on Sewer Network | SJ9655098550 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 409.17 | 99 | 99.93% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COTEBROOK STW | COTEBROOK WwTW | 016810067 | 16810067 | SO | Inlet CSO at WwTW | SJ5735065640 | GB112068060450 | Darley Brook | SANDYFORD BROOK |  |  | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | COTEHILL WWTW | Cote Hill Wastewater Treatment Works (COTHL) (017670051) | 017670051 | 17670051 | ST | Storm Tank at WwTW | NY4692050960 | GB102076073910 | Pow Maughan Beck | POW MAUGHAN BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 394.91 | 65 | 99.7% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | COTTENHAM LANE CSO 372RZ | Cottenham Lane CSO | 01SAL0081 | SAL0081 | SO | CSO on Sewer Network | SJ8337099340 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2017 - full year data expected | 37.13 | 16 | 100%
United Utilities | COTTON HALL STREET CSO | COTTON HALL STREET CSO | 01BBN0117 | BBN0117 | SO | CSO on Sewer Network | SD6925022850 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 23.03 | 59 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | COW HILL CLARKSONS FOLD CSO 33100 | Cow Hill Lane, Preston CSO (33100) | 017190863 | PRE0015 | SO | CSO on Sewer Network | SD5705034030 | GB112071065470 | Savick Brook | SAVICK BROOK TRIB RVR RIBBLE | n/a | n/a | Commissioned in 2018 - full year data expected | 51.26 | 5 | 100%
United Utilities | COWDE RD BR. | Cowpe Road SSO | 01ROS0042 | ROS0042 | SO | CSO on Sewer Network | SD8344021730 | GB112069064660 | Irwell (Source to Whitewell Brook) | 0 | N/A | N/A | Commissioned in 2019 - full year data expected | 3.2 | 4 | 100%
United Utilities | COWLING BROW CSO CHORL | Cowling Brow CSO | 01CHR0009 | CHR0009 | SO | CSO on Sewer Network | SD5956016940 | GB112070064951 | Yarrow US Big Lodge Water | BLACK BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 265.9 | 75 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COWLING FARM CSO | Cowling Farm CSO | 01CHR0007 | CHR0007 | SO | CSO on Sewer Network | SD5577114819 | GB112070064952 | Yarrow DS Big Lodge Water | CLANCUTT BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 1053.42 | 60 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | COWLING LANE LEYLAND LANE CSO 401PW | Cowling Lane/Leyland Lane CSO | 01SRI0017 | SRI0017 | SO | CSO on Sewer Network | SD5250022090 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2017 - full year data expected | 346.67 | 86 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | COWLISHAW CSO | Cowlishaw CSO | 016982851 | OLD0086 | SO | CSO on Sewer Network | SD9313008350 | GB112069061161 | Irk (Sourtce to Wince Brook) | LUZLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 17.7 | 8 | 100%
United Utilities | CRAB ST/DUKE ST | Cooper Street | 01STH0073 | STH0073 | SO | CSO on Sewer Network | SJ5075095760 | GB112069061210 | Hardshaw (Windle) Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CRAG BANK PUMPING STATION | Crag Bank PS | 017280249 | LAN0062 | SO | Storm Discharge at Pumping Station | SD4871070000 | 185 | #N/A | TRIB BLACK DYKE | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 21.9 | 8 | 100%
United Utilities | CRAKE VALLEY WWTW | CRAKE VALLEY WwTW | EPRFP3828GS | EPRFP3828GS | SO | Inlet CSO at WwTW | SD3141682708 | 181 | #N/A | RIVER CRAKE | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | CRANBERRY LANE CSO | Cranberry Lane CSO | 017180469 | BBN0143 | SO | CSO on Sewer Network | SD7021021080 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 1.33 | 7 | 100%
United Utilities | CRANBERRY LODGE PUMPING STATION | Cranberry Lodge Pumping Station (Site ID 50003) (WIG0162) | 01WIG0162 | WIG0162 | SO | Storm Discharge at Pumping Station | SD5698001890 | GB112070061610 | Poolstock Brook | PARK BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 14.03 | 8 | 100%
United Utilities | CRANKWOOD ROAD PUMPING STATION | Crankwood Road PS | 016993851 | WIG0129 | SO | Storm Discharge at Pumping Station | SD6175000190 | GB112069064520 | Hey/Borsdane Brook | TRIBUTARY OF HEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 8.05 | 3 | 99.99%
United Utilities | CRAWFORD STREET (NELSON) CSO 321P3 | CRAWFORD STREET (Nelson) CSO | 01PEN0008 | PEN0008 | SO | CSO on Sewer Network | SD8620038380 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0.17 | 2 | 100%
United Utilities | CREWE ROAD MILL LANE CSO 138CG | CREWE ROAD / MILL LANE CSO | 01CON0044 | CON0044 | SO | CSO on Sewer Network | SJ7512059070 | GB112068055420 | Wheelock (including Hassall Brook) | RIVER WHEELOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | CREWE WWTW | CREWE WwTW | 016810068 | 16810068 | ST | Storm Tank at WwTW | SJ6664057110 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 1981.63 | 109 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - December
United Utilities | CROASDALE AVENUE CSO | CROASDALE AVENUE CSO | 01COP0043 | COP0043 | SO | CSO on Sewer Network | NX9803015940 | 356 | #N/A | POW BECK | N/A | N/A | Commissioned in 2017 - full year data expected | 7.1 | 7 | 100%
United Utilities | CROFT CLOSE COMBINED SEWER OVERFLOW | The College CSO | 01EDE0007 | EDE0007 | SO | CSO on Sewer Network | NY5534041150 | GB102076073840 | Raven Beck | RAVEN BECK,TRIB OF RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 38.67 | 48 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CROFT DRV SHORE RD CSO CALDY 512RB | Croft Drive/Shore Road CSO | CG037860101 | WIR0093 | SO | CSO on Sewer Network | SJ2223084820 | 166 | #N/A | RIVER DEE ESTUARY | N/A | N/A | Commissioned in 2016 - full year data expected | 0.04 | 2 | 34.35% | Sensor failure / issue | Resolved - November
United Utilities | CROFT LN MANCHESTER RD CSO BOL0206 | Croft Lane / Manchester Road CSO | 016941054 | BOL0206 | SO | CSO on Sewer Network | SD7249207985 | GB112069064540 | Middle Brook | JENNY BECK CULVERT RIVER CROAL | n/a | n/a | Commissioned in 2018 - full year data expected | 1.73 | 7 | 100%
United Utilities | CROMFORD AVENUE CSO 451P7 | Cromford Avenue CSO | 016940200 | TRA0067 | SO | CSO on Sewer Network | SJ7879095370 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK TRIB SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 0.47 | 1 | 100%
United Utilities | CROMWELL ROAD/LICHFIELD STREET CSO | CROMWELL ROAD / LICHFIELD STREET CSO | 01SAL0028 | SAL0028 | SO | CSO on Sewer Network | SD8210000300 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.9 | 8 | 100%
United Utilities | CROSBY GARRET WWTW | Crosby Garret WwTW | 017670005 | 17670005 | SO | Inlet CSO at WwTW | NY7277010050 | GB102076070790 | Blind Beck | CROSBY GARRETT BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 4163.82 | 225 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | CROSBY ON EDEN PUMPING STATION | Low Crosby PS | 017680321 | CAR0076 | SO | Storm Discharge at Pumping Station | NY4458059300 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | CROSS STREET CSO | Cross Street CSO | 016982777 | WIG0193 | SO | CSO on Sewer Network | SD6149004420 | GB112069064520 | Hey/Borsdane Brook | CULVRTD SECTION HOCKERY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.13 | 1 | 100%
United Utilities | CROSSCANONBY WWTW CROSC | CROSSCANONBY WwTW | 017570086 | 17570086 | ST | Storm Tank at WwTW | NY0649038840 | 357 | #N/A | SCAD BECK | SILLOTH | Allonby South | Commissioned in 2016 - full year data expected | 562.47 | 63 | 99.42% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CROSTON ROAD CSO | Croston Road CSO | 017290494 | WYR0038 | SO | CSO on Sewer Network | SD4911045170 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 124.2 | 85 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CROSTON WWTW CRSTN | CROSTON WwTW | 017060017 | 17060017 | ST | Storm Tank at WwTW | SD4797018660 | GB112070064861 | Yarrow Culbeck Brook to tidal | RIVER YARROW | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2017 - full year data expected | 1484.43 | 102 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CROW WOOD CSO 08070 | Crow Wood Farm CSO | 01BUR0016 | BUR0016 | SO | CSO on Sewer Network | SD8329033570 | GB112071065120 | Calder - conf Brun to Pendle Water | RIVER CALDER | n/a | n/a | Commissioned in 2020 - full year data expected | 550.93 | 96 | 96.05% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CROWLANDS STREET PUMPING STATION | Crowland Street PS | 016931043 | SEF0067 | SO | Storm Discharge at Pumping Station | SD3671016650 | GB112070064830 | Three Pool's Waterway | THREE POOLS WATERWAY | Ribble | Southport | Commissioned in 2016 - full year data expected | 14.52 | 33 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | CROWN STREET (TOWN DYKE ORCHARD | Crown Street (Town Dyke Orchard) Sewer | 017670204 | CAR0042 | SO | CSO on Sewer Network | NY3968055830 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Commissioned in 2018 - full year data expected | 36.1 | 33 | 100%
United Utilities | CROWN STREET CSO 071QI | CROWN STREET CSO | 01BOL0121 | BOL0121 | SO | CSO on Sewer Network | SD7182009420 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Commissioned in 2018 - full year data expected | 148.17 | 92 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CROXTETH HALL LANE CSO 261QD | CROXTETH HALL LANE CSO | 01LIV0014 | LIV0014 | SO | CSO on Sewer Network | SJ4050094950 | GB112069060580 | Alt | RIVER ALT | N/A | N/A | Commissioned in 2018 - full year data expected | 3.77 | 3 | 78.29% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | CSO ADJ TO NUMBER 214 RAKE LANE | Rake Lane CSO | 016993808 | SAL0102 | SO | CSO on Sewer Network | SD7915101871 | GB112069061451 | Irwell (Croal to Irk) | SLACK BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 218.98 | 36 | 100%
United Utilities | CSO ADJACENT TO CARGO WWTW CARGO | CSO adjacent to Cargo WwTW | 01CAR0016 | CAR0016 | SO | CSO on Sewer Network | NY3599058850 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Commissioned in 2017 - full year data expected | 157.63 | 65 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CSO AT 18/20 BEECH FARM DRIVE | 18/20 Beech Farm Drive CSO | 016892097 | MAC0063 | SO | CSO on Sewer Network | SJ9154074560 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | CSO SOUTH OF ASHAWE GROVE | South of Ashawe Grove CSO | 016982741 | SAL0150 | SO | CSO on Sewer Network | SD7156003030 | GB112069061100 | Astley Brook (Mersey) | TRIB OF HONKSFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 176.13 | 56 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | CSO SOUTH OF ASHAWE GROVE | South of Ashawe Grove CSO | 016982742 | SAL0151 | SO | CSO on Sewer Network | SD7156003030 | GB112069061100 | Astley Brook (Mersey) | TRIBUTARY OF HONKSFORD BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.83 | 4 | 100%
United Utilities | CSO UPSTREAM OF BRAMPTON WWTW | Brampton CSO (Upstream of Carlisle WwTW) | NPSWQD002928 | CAR0095 | SO | CSO on Sewer Network | NY5087260894 | GB102076073981 | Irthing DS Crammel Linn Waterfall | BRAMPTON BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 19.37 | 20 | 100%
United Utilities | CUDDINGTON LANE CSO (471QL) | Cuddington Lane (adjacent Pipe Bridge) CSO | 01VRY0053 | VRY0053 | SO | CSO on Sewer Network | SJ5990072500 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 21.4 | 23 | 92.73%
United Utilities | CUDDINGTON LANE CSO (471QL) | Cuddington Lane (Woods) CSO | 01VRY0054 | VRY0054 | SO | CSO on Sewer Network | SJ5990072500 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | CUDDINGTON PUMPING STATION | Cuddington Pumping Station | EPRMB3297AV | CRE0087 | SO | Storm Discharge at Pumping Station | SJ5986072515 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON (CLIFFE) BROOKE | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | CUERDALE LANE CSO 401QM | CUERDALE LANE CSO | 01SRI0026 | SRI0026 | SO | CSO on Sewer Network | SD5654028480 | GB112071065500 | Ribble - conf Calder to tidal | RIVER RIBBLE | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | CULCETH LANE CSO | Culcheth Lane CSO | 016982731 | MAN0313 | SO | CSO on Sewer Network | SJ8840099430 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.37 | 1 | 99.73%
United Utilities | CULGAITH STW | CULGAITH WwTW | 017670167 | 17670167 | ST | Storm Tank at WwTW | NY6010029500 | GB102076070980 | Eden Lyvennet to Eamont | RIVER EDEN | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | CUMBERLAND STREET CSO | Cumberland Street CSO | NPSWQD010680 | BBN0016 | SO | CSO on Sewer Network | SD6887027440 | GB112071065310 | Blakewater | QUEENS PARK CULVERT VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 167.01 | 71 | 99.72% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | CUMBERLAND STREET CSO | Cumberland Street CSO | 016993736 | TAM0101 | SO | CSO on Sewer Network | SJ9590098800 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | CULVERT TO THE RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 5.1 | 12 | 100%
United Utilities | D/S 56 BARROW BRIDGE ROAD CSO | Downstream of No. 56 Barrow Bridge Road CSO | 016950315 | BOL0055 | SO | CSO on Sewer Network | SD6898011660 | GB112069064560 | Astley Brook (Irwell) | DEAN BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Comms failure / issue | N/A - Ongoing investigation
United Utilities | DACRE STW | Manchester Road (Greenfield) CSO | 017670081 | OLD0137 | SO | CSO on Sewer Network | NY4582026220 | GB102076070940 | Dacre Beck (Lower) | DACRE BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | DAISY LANE CSO | DAISY LANE CSO | 01BBN0033 | BBN0033 | SO | CSO on Sewer Network | SD6903028610 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DALE STREET CSO 331R7 | Dale Street CSO | 017180527 | PRE0105 | SO | CSO on Sewer Network | SD5528028750 | 176 | #N/A | RIVER RIBBLE TIDAL | Ribble | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | DALSTON ROAD PS | Dalston Sewage PS, CSO | 017680318 | CAR0077 | SO | Storm Discharge at Pumping Station | NY3861054060 | GB102076073880 | Caldew d/s Caldbeck | FAIRY BECK CULVERT | n/a | n/a | Commissioned in 2018 - full year data expected | 70.48 | 18 | 99.68%
United Utilities | DALSTON WWTW | DALSTON WwTW | 017670115 | 17670115 | ST | Storm Tank at WwTW | NY3796051170 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | n/a | n/a | Commissioned in 2018 - full year data expected | 430.87 | 28 | 82.8% | Sensor failure / issue | Resolved - December
United Utilities | DALTON SCREENS CSO | Dalton Screens | 017470006 | BRW0074 | SO | CSO on Sewer Network | SD2232073490 | GB112074069790 | Mill Beck (Poaka Beck) | POAKA BECK | WALNEY EAST | N/A | Commissioned in 2016 - full year data expected | 101.84 | 55 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | DAM HEAD BRIDGE /GISBURN ROAD CSO | Dam Head Bridge CSO | 01PEN0026 | PEN0026 | SO | CSO on Sewer Network | SD8763047040 | GB112071065540 | Stock Beck | BUTTS BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.5 | 6 | 100%
United Utilities | DAMSIDE | Damside Screening Chamber | 017280381 | LAN0113 | SO | CSO on Sewer Network | SD4757062060 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DAMSIDE SCREENING CSO 25076 | Damside Screening Chamber CSO | 017280278 | LAN0078 | SO | CSO on Sewer Network | SD4754062030 | 178 | #N/A | MILL RACE | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 109.14 | 31 | 99.91%
United Utilities | DANE AVENUE/WHEATCLOSE ROAD CSO | Dane Avenue/Wheatclose Road CSO | 01BRW0035 | BRW0035 | SO | CSO on Sewer Network | SD2194069334 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | Walney and Roose Beck | n/a | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | DANE BANK ROAD CSO 481QY | Dane Bank Road CSO | 01WAR0068 | WAR0068 | SO | CSO on Sewer Network | SJ6820087520 | 169 | #N/A | SLITTEN BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 268.43 | 84 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DANE STREET CSO 131Q1 | DANE STREET CSO | 01CON0001 | CON0001 | SO | CSO on Sewer Network | SJ8542063220 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | DANEFIELD ROAD CSO 45052 | The Danefield Road CSO | 016982773 | TRA0086 | SO | CSO on Sewer Network | SJ7928093210 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY (UNDER M63) | n/a | n/a | Commissioned in 2017 - full year data expected | 22.28 | 12 | 99.98%
United Utilities | DANES AVENUE CSO | Danes Avenue Combined Sewer Overflow (50112) (WIG0250) | NPSWQD006482 | WIG0250 | SO | CSO on Sewer Network | SD6210004720 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 691.44 | 98 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DANS ROAD WEATES CLOSE CSO 201Q2 | Dans Road/Weates Close | 01HAL0041 | HAL0041 | SO | CSO on Sewer Network | SJ5395085220 | 170 | #N/A | RIVER MERSEY VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 154.07 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DANTZIC ST WARFORD ST CSO 288A7 | DANTZIC STREET / WARFORD STREET CSO | 01MAN0039 | MAN0039 | SO | CSO on Sewer Network | SJ8460099540 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2018 - full year data expected | 0.53 | 1 | 100%
United Utilities | DANTZIC STREET CSO | Dantzic Street CSO | 016982951 | MAN0348 | SO | CSO on Sewer Network | SJ8465099560 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.3 | 2 | 100%
United Utilities | DARBY LANE CSO | Darby Lane CSO | 016982776 | WIG0192 | SO | CSO on Sewer Network | SD6146004480 | GB112069064520 | Hey/Borsdane Brook | HOCKERY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.23 | 14 | 100%
United Utilities | DARCY LEVER OLD HALL CSO | Darcy Lever Old Hall CSO | 01BOL0165 | BOL0165 | SO | CSO on Sewer Network | SD7458007770 | GB112069064550 | Croal (including Blackshaw Brook) | BLACKSHAW BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 32.6 | 21 | 99.99%
United Utilities | DARESBURY COMBINED SEWER OVERFLOW | Daresbury CSO | 016921415 | HAL0089 | SO | CSO on Sewer Network | SJ5784483338 | GB112068060520 | Keckwick Brook | DITCH TRIBUTARY RIVER MERSEY | N/A | N/A | Commissioned in 2019 - full year data expected | 1.2 | 4 | 81.51% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | DARK LANE CSO 441SH | DARK LANE CSO | 01TAM0089 | TAM0089 | SO | CSO on Sewer Network | SD9765002610 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | UNNAMED TRIB RIVER TAME | N/A | N/A | Commissioned in 2018 - full year data expected | 38.93 | 18 | 100%
United Utilities | DARWEN WWTW | DARWEN WwTW | 017160025 | 17160025 | ST | Storm Tank at WwTW | SD6898024200 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 964.02 | 80 | 99.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DAUB HALL LANE CSO 403CW | Daub Hall Lane, Walton-le-Dale CSO | 01LA1606 | SRI0015 | SO | CSO on Sewer Network | SD5910027280 | GB112071065280 | Many Brooks | BLACK BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 312.77 | 83 | 99.49% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | DAVYHULME ROAD EAST | Davyhulme Road East | 016982694 | TRA0081 | SO | CSO on Sewer Network | SJ8003094950 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DAVYHULME WWTW | DAVYHULME WwTW | 016940143 | 16940143 | ST | Storm Tank at WwTW | SJ7480096460 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | DEAN ROAD CSO 278A2 | Dean Road CSO | EPRJB3299AW | MAC0067 | SO | CSO on Sewer Network | SJ8630082781 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Commissioned in 2018 - full year data expected | 0.13 | 4 | 100%
United Utilities | DEAN STREET CSO (471RJ) | Dean Street CSO | 01VRY0006 | VRY0006 | SO | CSO on Sewer Network | SJ6553066360 | GB112068060460 | Weaver (Marbury Brook to Dane) | CULVERT TRIB DENE BROOK VIASWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.13 | 1 | 100%
United Utilities | DEAN VILLAGE WW PUMPING STATION | Dean Ww PS | 017570033 | ALL0102 | SO | Storm Discharge at Pumping Station | NY0665225052 | GB112075070540 | Marron | NEAR STOCK BECK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | DEAN WOOD CSO | Dean Wood CSO(49202) (WLN0020) | 017091504 | WLN0020 | SO | CSO on Sewer Network | SD5252005510 | GB112070064820 | Douglas - Lower | DEAN BROOK TRIB OF R DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 514.51 | 85 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | DEANSCALES PS & CSO | Deanscales PS and CSO | 017570034 | ALL0121 | SO | Storm Discharge at Pumping Station | NY0922026470 | GB112075070540 | Marron | TRIB OF FAR STOCK BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 389.22 | 61 | 88.36% | Sensor failure / issue | Resolved - August | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DEARDENGATE/BURY ROAD CSO | DEARDENGATE / BURY ROAD CSO | 01ROS0039 | ROS0039 | SO | CSO on Sewer Network | SD7808023251 | GB112069064650 | Ogden | SWINNEL BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DEARHAM WASTEWATER TREATMENT WORKS | DEARHAM WwTW | 017570068 | 17570068 | SO | Inlet CSO at WwTW | NY0704036760 | GB112075073640 | Ellen (lower) | RIVER ELLEN | Silloth | Allonby | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | Investigation now complete, remedial work due
United Utilities | DELPH NEW ROAD/STATION APPROACH CSO | Delph New Road/Station SSO | 016982525 | OLD0009 | SO | CSO on Sewer Network | SD9873007430 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 2037.17 | 205 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | DENT ROAD COMIBINED SEWER OVERFLOW | Dent Road CSO | 01COP0037 | COP0037 | SO | CSO on Sewer Network | NY0075008870 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Commissioned in 2016 - full year data expected | 10.8 | 32 | 100%
United Utilities | DENT STW | DENT WwTW | 017270015 | 17270015 | SO | Inlet CSO at WwTW | SD7021087350 | GB112072071680 | Dee - conf Deepdale Bk to conf Rawthey | TRIB RIVER DEE | N/A | N/A | Commissioned in 2020 - full year data expected | 455.25 | 130 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled
United Utilities | DENTON TRANSFER PUMPING STATION | Denton Transfer PS | 016993917 | TAM0177 | ST | Storm Discharge at Pumping Station | SJ9227093380 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | DENTON TRANSFER PUMPING STATION | Denton Transfer PS | 016993917 | TAM0177 | SO | Storm Discharge at Pumping Station | SJ9227093380 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | DENVER AVENUE ALTON STREET CSO | DENVER AVENUE / ALTON STREET CSO | 01CRE0034 | CRE0034 | SO | CSO on Sewer Network | SJ6990055340 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 7.07 | 14 | 100%
United Utilities | DERBY RD BARROWS LANE CSO 203DC | Derby Road/Barrows Green Lane | 016920641 | HAL0038 | SO | CSO on Sewer Network | SJ5355087980 | 170 | #N/A | BARROWS GREEN BROOK SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 2.03 | 8 | 100%
United Utilities | DERBY STREET CSO (49200) | Derby Street CSO | 01WLN0029 | WLN0029 | SO | CSO on Sewer Network | SD4195008880 | GB112070064810 | Eller Brook | TRIB OF ELLER BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 6.71 | 15 | 99.99%
United Utilities | DESOTO ROAD CSO (201RQ) | DESOTO ROAD CSO | 01HAL0045 | HAL0045 | SO | CSO on Sewer Network | SJ5039083990 | 170 | #N/A | RIVER MERSEY | N/A | N/A | Commissioned in 2020 - full year data expected | 558.1 | 61 | 90.76% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DEXTER RD HEATON PARK RD CSO | Dexter Road/Heaton Park Road CSO | 016993739 | MAN0126 | SO | CSO on Sewer Network | SD8415004470 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 2.1 | 11 | 100%
United Utilities | DIBBS LANE CSO 381RT | O/S 32 Hall Road East CSO | 016982651 | SEF0096 | SO | CSO on Sewer Network | SD2955001650 | GB641211630001 | Mersey Mouth | RIVER MERSEY ESTUARY | North Wirral | n/a | Commissioned in 2017 - full year data expected | 122.2 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DIBBS LANE CSO 381RT | Dibbs Lane CSO | 016982649 | SEF0094 | SO | CSO on Sewer Network | SD2955001650 | GB641211630001 | Mersey Mouth | RIVER MERSEY ESTUARY | n/a | n/a | Commissioned in 2018 - full year data expected | 1.67 | 6 | 100%
United Utilities | DICKENS STREET CSO | Dickens Street CSO | 01BBN0018 | BBN0018 | SO | CSO on Sewer Network | SD6887027442 | GB112071065310 | Blakewater | QUEENS PARK CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 134.94 | 56 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | DINGLE COMBINED SEWER OVERFLOW | Dingle CSO | 016930978 | LIV0042 | SO | CSO on Sewer Network | SJ3570086900 | 167 | #N/A | MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 50.96 | 41 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DISLEY PS | Disley PS | 016982849 | MAC0161 | SO | Storm Discharge at Pumping Station | SJ9812085420 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | 758.4 | 118 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DOBCROSS NEW ROAD CSO | Dobcross New Road CSO | 016982509 | OLD0011 | SO | CSO on Sewer Network | SD9904006320 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 2.03 | 2 | 100%
United Utilities | DOCK ROAD SOUTH CSO | Dock Road South PS, Bromborough | 016810665 | WIR0131 | SO | Storm Discharge at Pumping Station | SJ3541084410 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 1248.42 | 114 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DOCK ROAD SPS | Dock Road Sewage PS | 016810823 | VRY0021 | SO | Storm Discharge at Pumping Station | SJ6568073230 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DOCK ST OVERFLOW | Dock Street CSO | 01WYR0028 | WYR0028 | SO | CSO on Sewer Network | SD3389047630 | 341 | #N/A | COPSE BROOK CULVERT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DOCK STREET CSO 52567 | MacDermott Road Pumping Station (formerly Dock Street PS) | 017290502 | HAL0111 | SO | Storm Discharge at Pumping Station | SD3363047580 | 341 | #N/A | COPSE BROOK CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 42.37 | 14 | 100%
United Utilities | DOCK STREET CSO 52567 | Dock Street Combined Sewer Overflow (Site ID 52567) (WYR0080) | 017290502 | WYR0080 | SO | CSO on Sewer Network | SD3363047580 | 341 | #N/A | COPSE BROOK CULVERT | Lune (Wyre Estuary) and Lune (Broadfleet and Plover Scar) | Fleetwood | Commissioned in 2019 - full year data expected | 1.99 | 4 | 100%
United Utilities | DOOLEY DRIVE CSO/ | Dooley Drive Combined Sewer Overflow (381N6) (SEF0065) ( Emergency Overflow for 38006 – Copy Lane Pumping Station | 016997071 | SEF0065 | SO | CSO on Sewer Network | SJ3697099830 | GB112069061441 | Alt US Bull Bridge | MOOR HEY BRK TRIB OF R. ALT | n/a | n/a | Commissioned in 2018 - full year data expected | 55.63 | 6 | 100%
United Utilities | DORCHESTER RD ADJ NO 182 MANCH CSO | Dorchester Rd, adj 182 Manchester Rd | 016982744 | SAL0154 | SO | CSO on Sewer Network | SD7770000620 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB FOLLY BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | DOVENBY WWTW DOVEN | Dovenby Waste water Treatment Works (DOVEN) (017570035) | 017570035 | 17570035 | ST | Storm Tank at WwTW | NY0895032850 | GB112075073570 | Broughton Beck | DOVENBY BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 121.62 | 26 | 99.62%
United Utilities | DOW BRIDGE CSO 19080 | Dow Bridge CSO (19080) | 017190860 | FYL0017 | SO | CSO on Sewer Network | SD4360031700 | GB112071065670 | Dow Brook | DOW BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 94.57 | 10 | 100%
United Utilities | DOWNS ROAD COMBINED SEWER OVERFLOW | Downs Road CSO | 016892108 | HAL0056 | SO | CSO on Sewer Network | SJ5163082730 | 169 | #N/A | BRIDGEWATER CANAL VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0.33 | 2 | 95.38%
United Utilities | DRAGONS TOOTH CSO | Hacken Lane CSO | 016982098 | BOL0114 | SO | CSO on Sewer Network | SD7339007880 | GB112069064550 | Croal (including Blackshaw Brook) | THE RIVER CROAL | N/A | N/A | Commissioned in 2019 - full year data expected | 629.38 | 84 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | DRAKE STREET CSO (35038) | Drake Street CSO | 01ROC0078 | ROC0078 | SO | CSO on Sewer Network | SD8976013400 | GB112069064720 | Roch (Source to Spodden) | CULVERTED RIVER ROCH VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 12.11 | 24 | 85.86% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | DRUMBURGH PUMPING STATION DRMBU | Drumburgh PS | 017680458 | ALL0137 | SO | Storm Discharge at Pumping Station | NY2674060070 | GB530207614700 | SOLWAY | TIDAL TRIB OF THE SOLWAY FIRTH | Solway | n/a | Commissioned in 2017 - full year data expected | 18.42 | 14 | 100%
United Utilities | DUBWATH WASTEWATER TREATMENT WORKS | DUBWATH WwTW | 017570036 | 17570036 | SO | Inlet CSO at WwTW | NY2001031190 | GB112075070500 | Wythop Beck | DUBWATH BECK | N/A | N/A | Commissioned in 2016 - full year data expected | 691.97 | 98 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | DUDDLE LANE CSO | Duddle Lane CSO | 017180617 | SRI0010 | SO | CSO on Sewer Network | SD5599026920 | GB112071065300 | Darwen - conf Roddlesworth to tidal | HENNEL BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | DUFTON VILLAGE STW | DUFTON WwTW | 017670010 | 17670010 | SO | Inlet CSO at WwTW | NY6879025320 | GB102076070960 | Swindale Beck nr Dufton | MILL BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 86.64 | 35 | 100%
United Utilities | DUKE STREET | Duke Street CSO | 01LAK0044 | LAK0044 | SO | CSO on Sewer Network | SD5171078500 | GB112073071050 | Holme Beck | HOLME BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DUKES BROW CSO | Dukes Brow Combined Sewer Overflow (Site ID 051SL) (BBN0069) | 01BBN0069 | BBN0069 | SO | CSO on Sewer Network | SD6730028610 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 7.43 | 24 | 89.32% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | DUKINFIELD OUTFALL SEWER CSO 441SM | Dukinfield Outfall Sewer CSO | 01TAM0150 | TAM0150 | SO | CSO on Sewer Network | SJ9327096700 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 4.6 | 14 | 100%
United Utilities | DUKINFIELD RD THROSTLE BANK ST CSO | Junction of Dukinfield Road and Throstle Bank Street combined sewer overflow (441SN) (TAM0079) | 01TAM0079 | TAM0079 | SO | CSO on Sewer Network | SJ9417095610 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | UNNAMED TRIB RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 1.03 | 2 | 100%
United Utilities | DUKINFIELD WWTW | DUKINFIELD WwTW | 016940087 | 16940087 | ST | Storm Tank at WwTW | SJ9326096730 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | DUKINFIELD WWTW | DUKINFIELD WwTW | 016940087 | 16940087 | SO | Inlet CSO at WwTW | SJ9326096730 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | DUMERS LANE PUMPING STATION | Dumers Lane PS | NPSWQD010892 | BRY0026 | SO | Storm Discharge at Pumping Station | SD8003008120 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 1.68 | 2 | 99.99%
United Utilities | DUMPLINGTON CIRCLE | Dumplington Circle CSO | 016982695 | TRA0085 | SO | CSO on Sewer Network | SJ7667097560 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | DUNHAM MASSEY OUTFALL CSO (451SS) | Dunham Massey Outfall SSO | 01TRA0079 | TRA0079 | SO | CSO on Sewer Network | SJ7269087541 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 250.17 | 57 | 89.57% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | DUNHAM MASSEY STW | DUNHAM MASSEY WwTW | 016940003 | 16940003 | ST | Storm Tank at WwTW | SJ7269087540 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | DUNSCAR BRIDGE CSO | Dunscar Bridge CSO (071SU) (BOL0176) | 016982205 | BOL0176 | SO | CSO on Sewer Network | SD7115013430 | GB112069064570 | Eagley Brook | EAGLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 841.83 | 116 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | #N/A | Duxbury Mill Farm PS | EPRSB3395VW | CHR0059 | SO | Storm Discharge at Pumping Station | SD5881715661 | GB112070064951 | Yarrow US Big Lodge Water | River Yarrow | N/A | N/A | Commissioned in 2019 - full year data expected | 18.3 | 7 | 99.5%
United Utilities | DYEHOUSE LANE CSO | Dyehouse Lane CSO | 016982937 | ROC0170 | SO | CSO on Sewer Network | SD9131015060 | GB112069064720 | Roch (Source to Spodden) | ASH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 10.97 | 20 | 100%
United Utilities | EAGLESFIELD WWTW EAGLE | EAGLESFIELD WwTW | 017570037 | 17570037 | ST | Storm Tank at WwTW | NY0975028480 | GB112075070400 | Cocker - conf Whit Beck to conf Derwent | DUBBS GUTTER | n/a | n/a | Commissioned in 2017 - full year data expected | 2761.29 | 227 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | EARLS WAY CSO 12066 | Earls Way CSO | 01CHR0002 | CHR0002 | SO | CSO on Sewer Network | SD5580018890 | GB112070064861 | Yarrow Culbeck Brook to tidal | CHAPEL BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 206.84 | 75 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | EAST GREENFIELD CSO | East Greenfield CSO | 016982923 | OLD0152 | SO | CSO on Sewer Network | SD9929004290 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 2.83 | 1 | 100%
United Utilities | EAST LANCS ROAD PUMPING STATION | East Lancs Road Pumping Station (EASTL) (WIG0179) | 01WIG0179 | WIG0179 | SO | Storm Discharge at Pumping Station | SD6992000140 | GB112069061100 | Astley Brook (Mersey) | ASTLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 31.8 | 20 | 100%
United Utilities | EAST OF COUNCIL OFFICE | East of Council Offices CSO | 01WYR0039 | WYR0039 | SO | CSO on Sewer Network | SD4937045420 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | N/A | Commissioned in 2020 - full year data expected | 315.64 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | EASTHAM RAKE CSO | Eastham Rake Combined Sewer Overflow (Site ID 51068) (WIR0111) | 016892412 | WIR0111 | SO | CSO on Sewer Network | SJ3483079350 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | DIBBINSDALE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 47.76 | 21 | 100%
United Utilities | EASTHAM VILLAGE CSO | Eastham Village CSO | 01WIR0110 | WIR0110 | SO | CSO on Sewer Network | SJ3650081800 | 171 | #N/A | MERSEY ESTUARY (TIDAL) | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 40.13 | 37 | 92.74%
United Utilities | EASTLAND FARM COMBINED SEWER O'FLOW | Eastland Farm CSO | 01ALL0017 | ALL0017 | SO | CSO on Sewer Network | NY0742039190 | 357 | #N/A | SCAD BECK TRIB OF SOLWAY EST'Y | SILLOTH | Allonby South | Commissioned in 2016 - full year data expected | 152.07 | 73 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | EATON BANK CSO 131S4 | Eaton Bank CSO | 01CON0004 | CON0004 | SO | CSO on Sewer Network | SJ8674063840 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | n/a | n/a | Commissioned in 2017 - full year data expected | 152.2 | 66 | 92.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | EAVES GREEN RD CSO | Eaves Green Road CSO | 01LA1964 | CHR0066 | SO | CSO on Sewer Network | SD5783015960 | GB112070064952 | Yarrow DS Big Lodge Water | TRIB RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 50.33 | 35 | 100%
United Utilities | EAVES GREEN RD CSO | Eaves Green Brook CSO | 01CHR0016 | CHR0016 | SO | CSO on Sewer Network | SD5783015960 | GB112070064952 | Yarrow DS Big Lodge Water | TRIB RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 11.47 | 14 | 100%
United Utilities | ECCLES STW | ECCLES WwTW | 016940144 | 16940144 | ST | Storm Tank at WwTW | SJ7496097150 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | ECCLES STW | ECCLES WwTW | 016940144 | 16940144 | SO | Inlet CSO at WwTW | SJ7496097150 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 772.33 | 125 | 98.18% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ECCLESTONE BRIDGE CSO 12065 | Eccleston Bridge D/S CSO | 017060128 | CHR0051 | SO | CSO on Sewer Network | SD5085017690 | GB112070064861 | Yarrow Culbeck Brook to tidal | RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 2313.46 | 130 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | EDENFIELD ROAD CSO | Edenfield Road CSO | EPRQB3593DY | ROC0070 | SO | CSO on Sewer Network | SD8579014610 | GB112069064710 | Naden Brook | NADEN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.6 | 5 | 100%
United Utilities | EDENHALL VILLAGE AND HOTEL WWTW | EDENHALL VILLAGE & HOTEL WwTW | 017670058 | 17670058 | SO | Inlet CSO at WwTW | NY5631032610 | GB102076073940 | Eden - Eamont to tidal | TRIB RIVER EDEN | n/a | n/a | Commissioned in 2019 - full year data expected | 1227.54 | 121 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | EDGE LANE/MANCHESTER ROAD/HIGH LANE | Edge Lane/Manchester Road/High Lane | 016982629 | MAN0315 | SO | CSO on Sewer Network | SJ8093693606 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | TRIB CHORLETON BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 1.13 | 3 | 100%
United Utilities | EDGE LANE/WILBRAHAM CSO | Edge Lane/Wilbraham Road CSO | 016993694 | MAN0228 | SO | CSO on Sewer Network | SJ8078093260 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 94.37 | 53 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | EDITH STREET CSO 078NL | Edith Street CSO | 01BOL0102 | BOL0102 | SO | CSO on Sewer Network | SD7054008870 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Commissioned in 2018 - full year data expected | 3.2 | 5 | 96.47%
United Utilities | EDLESTON ROAD NO 2 CSO | EDLESTON ROAD No1 CSO | 01CRE0040 | CRE0040 | SO | CSO on Sewer Network | SJ7052055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 6.53 | 17 | 89.32% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | EDLESTON ROAD NO 2 CSO | Edleston Road No 2 CSO | 016892253 | CRE0041 | SO | CSO on Sewer Network | SJ7052055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.07 | 3 | 100%
United Utilities | EDWARD STREET | Edward Street (Dunkinfield) CSO | 01TAM0074 | TAM0074 | SO | CSO on Sewer Network | SJ9355096350 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB OF RIVER TAME VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 30.5 | 41 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | EDWARD STREET CSO | EDWARD STREET CSO | 01PEN0005 | PEN0005 | SO | CSO on Sewer Network | SD8691039030 | GB112071065150 | Colne Water - Wanless Water to Pendle Water | SWINDEN CLOUGH | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | EGERTON ST WORSLEY ST CSO | Egerton Street / Worsley Street CSO | 016983277 | MAN0181 | SO | CSO on Sewer Network | SJ8279197530 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 101.6 | 77 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | EJEC STN, NEWBIGGIN-ON-LUNE | Newbiggin-on-Lune Wastewater Network Pumping Station | 01EDE0065 | EDE0065 | SO | Storm Discharge at Pumping Station | NY7034005380 | GB112072071760 | Lune - headwaters to conf Birk Beck | 0 | N/A | N/A | Commissioned in 2020 - full year data expected | 160.27 | 22 | 100%
United Utilities | ELLEN VALE CSO | Ellen Vale | 017580250 | ALL0093 | SO | CSO on Sewer Network | NY1490040800 | GB112075073640 | Ellen (lower) | RIVER ELLEN | n/a | n/a | Commissioned in 2018 - full year data expected | 305.53 | 74 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ELLESMERE PORT WWTW | ELLESMERE PORT WwTW | 016810030 | 16810030 | ST | Storm Tank at WwTW | SJ4320074650 | 168 | #N/A | THORNTON BROOK/RIVER GOWY | N/A | N/A | Commissioned in 2019 - full year data expected | 1261.62 | 96 | 99.97% |  |  | Data collection - EDM non-representative location | Resolved - October
United Utilities | ELLESMERE ROAD CSO 481TI | ELLESMERE ROAD CSO | 01WAR0059 | WAR0059 | SO | CSO on Sewer Network | SJ6128086390 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 12.8 | 13 | 100%
United Utilities | ELLESMERE STREET CSO | Ellesmere Street CSO | 016983324 | WIG0234 | SO | CSO on Sewer Network | SD6875102302 | GB112069060810 | Bedford Brook | SHAKERLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 24.03 | 31 | 100%
United Utilities | ELSWICK STW | ELSWICK WwTW | 017260053 | 17260053 | SO | Inlet CSO at WwTW | SD4105038170 | GB112072066110 | Thistleton Brook | THISTLETON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 949.67 | 301 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ELTERWATER PUMPING STATION | Elterwater pumping station (ELTER) (LAK0025) | 01LAK0025 | LAK0025 | SO | Storm Discharge at Pumping Station | NY3279004720 | GB112073071120 | Great Langdale Beck | GREAT LANGDALE BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 422.85 | 31 | 99.6%
United Utilities | ELTON PS | Elton PS | 01CHE0025 | CHE0025 | SO | Storm Discharge at Pumping Station | SJ4646075690 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | WEST CENTRAL DRAIN, MERSEY EST | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | EMBLETON WWTW | EMBLETON WwTW | 017570038 | 17570038 | ST | Storm Tank at WwTW | NY1795030530 | GB112075070500 | Wythop Beck | TRIB DUBWATH BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 4099.48 | 187 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ENNISDALE DRIVE CSO | Ennisdale Drive CSO | 016982966 | WIR0142 | SO | CSO on Sewer Network | SJ2293087780 | GB112068060530 | The Birket including Arrowe Brook and Fender | NEWTON BROOK | NORTH WIRRAL (WEST) | West Kirby | Commissioned in 2016 - full year data expected | 0.57 | 4 | 100%
United Utilities | ENTWISTLE ST CSO | Entwistle Street Combined Sewer Overflow (073DQ) (BOL0093) | 016983217 | BOL0093 | SO | CSO on Sewer Network | SD7269009850 | GB112069064530 | Tonge | RIVER TONGE | n/a | n/a | Commissioned in 2018 - full year data expected | 7.9 | 9 | 99.96%
United Utilities | ESK AVENUE MIREHOUSE CSO | Esk Avenue Mirehouse CSO | 017480429 | COP0041 | SO | CSO on Sewer Network | NX9788017180 | 356 | #N/A | UN-NAMED TRIB OF POW BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 20.07 | 19 | 99.98%
United Utilities | ESTER STREET CAR PARK CSO 203DR | Ester Street Car Park CSO | 016982703 | HAL0117 | SO | CSO on Sewer Network | SJ5214086050 | 170 | #N/A | BOWERS BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 19.8 | 16 | 59.37% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | ETTERBY TERRACE CSO | Etterby Terrace CSO | 01CAR0004 | CAR0004 | SO | CSO on Sewer Network | NY3963057050 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Commissioned in 2016 - full year data expected | 73.41 | 34 | 100%
United Utilities | EXPRESSWAY 8 RUNCORN | Expressway 8, Runcorn (Weston Point, Point R) CSO | 01HAL0061 | HAL0061 | SO | CSO on Sewer Network | SJ4977082450 | 169 | #N/A | MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 115.03 | 61 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | FACTORY LANE CSO | Factory Lane CSO | 01SRI0023 | SRI0023 | SO | CSO on Sewer Network | SD5399027460 | 175 | #N/A | BOUNDARY BROOK TRIB RIV RIBBLE | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 234.59 | 31 | 99.97%
United Utilities | FACTORY ST/CHARLES ST CSO | Factory Street/Charles Street CSO, Leigh | 016993530 | WIG0087 | SO | CSO on Sewer Network | SD6862002140 | GB112069060810 | Bedford Brook | HINDSFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 29.1 | 10 | 100%
United Utilities | FAILSWORTH WWTW | FAILSWORTH WwTW | 016983268 | 16983268 | ST | Storm Tank at WwTW | SJ8960099710 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | FAILSWORTH WWTW | FAILSWORTH WwTW | 016983268 | 16983268 | SO | Inlet CSO at WwTW | SJ8960099710 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | FAIRFIELD RD RUSSELL RD CSO 25026 | Fairfield Road/Russell Road CSO | 01LAN0070 | LAN0070 | SO | Storm Discharge at Pumping Station | SD5038070130 | GB112073064430 | Keer - Lower | CLVRT BACK LANE / KELLET RD | MORECAMBE BAY EAST | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | FAIRFIELD ST/STEVENSON ST EAST CSO | FAIRFIELD STREET / STEVENSON STREET EAST CSO | 01HYN0024 | HYN0024 | SO | CSO on Sewer Network | SD7494028100 | GB112071065040 | Hyndburn | CULV SECTION OF TINKER BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | FAIRFIELD STREET CSO | Fairfield Street CSO | 016982730 | MAN0309 | SO | CSO on Sewer Network | SJ8543097630 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 44.3 | 27 | 95.73%
United Utilities | FAIRFIELD STREET CSO | Fairfield Street CSO | 017060093 | SRI0007 | SO | CSO on Sewer Network | SD5481025110 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 4.33 | 6 | 100%
United Utilities | FAIRHAVEN PS | Fairhaven PS | 017180556 | FYL0042 | SO | Storm Discharge at Pumping Station | SD3353027230 | 176 | #N/A | RIVER RIBBLE | Ribble | St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 120.54 | 21 | 99.83%
United Utilities | FAIRHAVEN PS | Fairhaven PS | 017180556 | FYL0042 | SO | Storm Discharge at Pumping Station | SD3353027230 | 176 | #N/A | RIVER RIBBLE | Ribble | St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 26.09 | 9 | 99.83%
United Utilities | FAIRHILLS ROAD CSO (37002) | FAIRHILLS ROAD CSO | 01SAL0023 | SAL0023 | SO | CSO on Sewer Network | SJ7266093780 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 45.23 | 27 | 100%
United Utilities | FAIRY LANE CSO 281T3 | FAIRY LANE CSO | 01MAN0066 | MAN0066 | SO | CSO on Sewer Network | SJ8346099321 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 0.73 | 3 | 99.93%
United Utilities | FARM HILL CSO 091KO | Farm Hill CSO | 01BRY0038 | BRY0038 | SO | CSO on Sewer Network | SD8053003980 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH VIA CULVERT | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | FAZAKERLEY WWTW | FAZAKERLEY WwTW | 016930112 | 16930112 | ST | Storm Tank at WwTW | SJ3958096340 | GB112069060580 | Alt | RIVER ALT | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | FERN BANK CSO | FERN BANK CSO | 01TAM0126 | TAM0126 | SO | CSO on Sewer Network | SJ9723097940 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | STOCKS BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 55.53 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | FERN STREET CSO (078J3) | Fern Street CSO | 01BOL0146 | BOL0146 | SO | CSO on Sewer Network | SD7436006851 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | N/A | N/A | Commissioned in 2018 - full year data expected | 5.73 | 18 | 100%
United Utilities | FERNEYFIELD ROAD CSO OLD0104 | Ferneyfield Road Sewer | 016950498 | OLD0104 | SO | CSO on Sewer Network | SD8976505556 | GB112069061120 | Wince Brook | SPRING BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 5.4 | 7 | 100%
United Utilities | FERRY PUMPING STATION SITE ID 04528 | Ferry PS | 017480342 | BRW0099 | SO | Storm Discharge at Pumping Station | SD1878068750 | 169 | #N/A | MASSEY BROOK | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 492.47 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | FIELD EAST OF RIVER DARWIN CSO | Field East of River Darwin CSO | 017190837 | SRI0028 | SO | CSO on Sewer Network | SD5585027830 | GB112071065300 | Darwen - conf Roddlesworth to tidal | RIVER DARWIN | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 1157.4 | 129 | 97.56% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | FIELD HEAD PUMPING STATION LAK0090 | Field Head Pumping Station (Site ID FLDHD) (LAK0090) | 017380283 | LAK0090 | SO | Storm Discharge at Pumping Station | SD3660075500 | 181 | #N/A | TRIB WINDERMOOR MAIN DRAIN | MORECAMBE BAY (LEVEN) | N/A | Commissioned in 2018 - full year data expected | 2233.96 | 164 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | FIELD NO.4649 OFF KEELE ROAD CSO | Field No. 4649 (off Keele Road) CSO | 01NEW0007 | NEW0007 | SO | CSO on Sewer Network | SJ7838045470 | GB112068055230 | Checkley Brook - Upper | HAZELEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.07 | 1 | 100%
United Utilities | FIELDEN STREET CSO | Fielden Street CSO | 017180518 | BBN0154 | SO | CSO on Sewer Network | SD6752027800 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | FIELDING STREET CSO (ROC0193) | Fielding Street CSO | EPRJB3892VC | ROC0193 | SO | CSO on Sewer Network | SD8734506810 | GB112069061161 | Irk (Sourtce to Wince Brook) | CLV TRIB OF WHIT BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | FINN AVENUE COMBINED SEWER OVERFLOW | Finn Avenue CSO | 01CAR0013 | CAR0013 | SO | CSO on Sewer Network | NY3926055620 | GB102076073880 | Caldew d/s Caldbeck | DOW BECK CULVERT | N/A | N/A | Commissioned in 2018 - full year data expected | 4.97 | 8 | 92.11%
United Utilities | FIR LANE COMBINED SEWER OVERFLOW | FIR LANE CSO | 01OLD0019 | OLD0019 | SO | CSO on Sewer Network | SD9197009000 | GB112069061161 | Irk (Sourtce to Wince Brook) | UNNAMED TRIBUTARY OF RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 37.73 | 52 | 90.34% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | FIR TREE AVENUE PUMPING STATION | Fir Tree Avenue PS | 01SAL0001 | SAL0001 | SO | Storm Discharge at Pumping Station | SD7247000210 | GB112069061090 | Shaw Brook | SNIGGLEY DITCH | N/A | N/A | Commissioned in 2018 - full year data expected | 2.8 | 5 | 99.96%
United Utilities | FIRS LANE/URMSTON STREET CSO | FIRS LANE / URMSTON STREET CSO | 01WIG0066 | WIG0066 | SO | CSO on Sewer Network | SD6482000240 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | FIRST AVENUE CSO | First Avenue CSO | 016993654 | MAN0178 | SO | CSO on Sewer Network | SJ7975097470 | GB112069061161 | Irk (Sourtce to Wince Brook) | PLUMPTON CLOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 0.78 | 3 | 99.52%
United Utilities | FISHERGATE HILL CSO (CHAMBER C9) | Fishergate Hill CSO | 017190875 | PRE0022 | SO | CSO on Sewer Network | SD5286928868 | 176 | #N/A | RIVER RIBBLE | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | FISHERGATE HILL CSO CHAMBER C8 | Fishergate Hill CSO | 017190876 | PRE0027 | SO | CSO on Sewer Network | SD5283728977 | 176 | #N/A | RIVER RIBBLE | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | FITZ BRIDGE (LOW ROAD) CSO | Fitz Bridge (Low Road) CSO | 017571047 | ALL0063 | SO | CSO on Sewer Network | NY1068030860 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 1005.04 | 91 | 99.53% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | FLAG LANE N0 2 CSO 165JH | FLAG LANE No1 CSO | 01CRE0036 | CRE0036 | SO | CSO on Sewer Network | SJ7003055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 19.9 | 20 | 94.15%
United Utilities | FLAG LANE N0 2 CSO 165JH | FLAG LANE NO2 CSO | 01CRE0037 | CRE0037 | SO | CSO on Sewer Network | SJ7003055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 16.23 | 7 | 100%
United Utilities | FLASS LANE AT BRIDGEGATE CSO | Flass Lane at Bridgegate Ave, Newbarns CSO (04531/04CSO009) | 01BRW0039 | BRW0039 | SO | CSO on Sewer Network | SD2194069335 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | Walney and Roose Beck | n/a | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | FLEET STREET | Fleet Street CSO | 017180622 | PEN0081 | SO | CSO on Sewer Network | SD8600038550 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 23.28 | 5 | 99.99%
United Utilities | FLETCHERTOWN STW | FLETCHERTOWN WwTW | 017570014 | 17570014 | ST | Storm Tank at WwTW | NY2125043500 | GB102075073480 | Crummock Beck u/s Holme Dub | CRUMMOCK BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 5777.15 | 291 | 100% |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation
United Utilities | FLIXTON ROAD CSO | Flixton Road CSO | 01TRA0039 | TRA0040 | SO | CSO on Sewer Network | SJ7449093850 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2018 - full year data expected | 37.53 | 13 | 100%
United Utilities | FLIXTON ROAD CSO | Flixton Road/Irlam Road Flixton Combined Sewer Overflow (451UM) (TRA0039) | 01TRA0039 | TRA0039 | SO | CSO on Sewer Network | SJ7449093850 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | FOLDS ROAD COMBINED SEWER OVERFLOW | Folds Road CSO | 016993696 | STH0064 | SO | CSO on Sewer Network | SJ5372096100 | GB112069061230 | Black Brook (Mersey Estuary) | BLACK BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 535 | 102 | 98.26% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | FOOTPATH NR CROSS ST CSO | Footpath Near Cross Street CSO | 017190822 | BBN0106 | SO | CSO on Sewer Network | SD6975021230 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0.03 | 1 | 93.85%
United Utilities | FOOTWOOD / SPODDEN VALLEY CSO | Shawclough Brook CSO | 016982516 | ROC0169 | SO | CSO on Sewer Network | SD8870014380 | GB112069064730 | Spodden | RIVER SPODDEN, TRIB RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 368.38 | 59 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | FORGE MILL PS | Forge Mill PS | 01STA0098 | STA0098 | SO | Storm Discharge at Pumping Station | SJ8879059710 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 26.4 | 18 | 100%
United Utilities | FORMBY WASTEWATER TREATMENT WORKS | FORMBY WwTW | 016930108 | 16930108 | ST | Storm Tank at WwTW | SD2971005900 | GB112069061442 | Alt DS Bull Bridge | RIVER ALT | RIBBLE | Formby | Commissioned in 2016 - full year data expected | 981.47 | 98 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | FOWLER LANE/CROSTON ROAD CSO | FOWLER LANE / CROSTON ROAD CSO | 01SRI0025 | SRI0025 | SO | CSO on Sewer Network | SD5398024860 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 54.77 | 22 | 100%
United Utilities | FOXDENTON LANE CSO | Foxdenton Lane CSO | 016983136 | OLD0163 | SO | CSO on Sewer Network | SD8957004540 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 158.73 | 73 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | FOXFIELD SEWAGE PUMPING STATION | Foxfield PS | 017480180 | LAK0097 | SO | Storm Discharge at Pumping Station | SD2096085270 | GB531207411800 | DUDDON | DUDDON ESTUARY | N/A | N/A | Commissioned in 2016 - full year data expected | 340.08 | 28 | 99.59%
United Utilities | FRANK WEBB AVENUE CSO | Frank Webb Avenue CSO | 016810300 | CRE0026 | SO | CSO on Sewer Network | SJ6931056820 | GB112068060460 | Weaver (Marbury Brook to Dane) | LEIGHTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 8.99 | 7 | 100%
United Utilities | FRANKBY CLOSE CSO 513MM | Frankby Close CSO | 01WIR0087 | WIR0087 | SO | CSO on Sewer Network | SJ2481087060 | GB112068060530 | The Birket including Arrowe Brook and Fender | GREASBY BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 21.4 | 35 | 98.75%
United Utilities | FRANKS BRIDGE CSO (171UZ) | Franks Bridge SSO | 017680272 | EDE0077 | SO | CSO on Sewer Network | NY7764008720 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 407.47 | 73 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | FREDERICK ROAD CSO (371UV) | Frederick Road CSO | 016940467 | SAL0140 | SO | CSO on Sewer Network | SJ8216099790 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2020 - full year data expected | 37.4 | 25 | 100%
United Utilities | FREDERICK ST PS | Frederick Street Pumping Station | 017480412 | BRW0044 | SO | Storm Discharge at Pumping Station | SD2123068810 | 340 | #N/A | MILL BECK/ CAVENDISH DOCK | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 108.38 | 27 | 100%
United Utilities | FRENCH STREET CSO 201UW | French Street CSO | 01HAL0043 | HAL0043 | SO | CSO on Sewer Network | SJ5395085222 | 170 | #N/A | RIVER MERSEY VIA SWS | n/a | n/a | Commissioned in 2017 - full year data expected | 290.07 | 70 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | FRENCHWOOD KNOLL CSO 331UX | Frenchwood Knoll CSO | 017180524 | PRE0104 | SO | CSO on Sewer Network | SD5425028690 | 176 | #N/A | SWILLBROOK CULVERT | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 59.7 | 83 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | FRIDAY STREET CSO 121UY | FRIDAY STREET CSO | 01CHR0010 | CHR0010 | SO | CSO on Sewer Network | SD5820017890 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER CHOR | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | FRONT STREET CSO 13521 | FRONT STREET CSO | 01CON0047 | CON0047 | SO | CSO on Sewer Network | SJ7611060680 | GB112068055430 | Arclid Brook | ARCLID BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | FULSHAW CROSS CSO 271U4 | Fulshaw Cross CSO | 016982621 | MAC0157 | SO | CSO on Sewer Network | SJ8419079580 | GB112069061330 | Mobberley Brook | WHITEHALL BROOK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 119.67 | 58 | 100% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation
United Utilities | FULWELL AVENUE CSO | Fulwell Avenue CSO | 016982785 | WIG0205 | SO | CSO on Sewer Network | SD6815002000 | GB112069060810 | Bedford Brook | HINDSFORD BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 424.84 | 59 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | FULWOOD CSO | Fulwood CSO | 016930980 | LIV0043 | SO | CSO on Sewer Network | SJ3720086000 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 0.55 | 2 | 100%
United Utilities | GALLOPER POOL PS | Galloper Pool PS | 017680341 | EDE0093 | SO | Storm Discharge at Pumping Station | NY6150004601 | GB112072071720 | Lune - conf Birk Beck to conf Rawthey | GALLOPER POOL | N/A | N/A | Commissioned in 2019 - full year data expected | 9.56 | 4 | 100%
United Utilities | GAMBLESBY PUMPING STATION | Gamblesby PS | 017680387 | EDE0112 | SO | Storm Discharge at Pumping Station | NY6052039500 | GB102076073820 | Glassonby Beck | GAMBLESBY BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 280.49 | 51 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GAMBREL BANK ROAD CSO 441U7 | Gambrel Bank Road CSO | 01TAM0050 | TAM0050 | SO | CSO on Sewer Network | SD9374000740 | GB112069061151 | Medlock (Source to Lumb Brook) | DOWNSHAW BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 2.3 | 6 | 95.66%
United Utilities | GARDNER ROAD PUMPING STATION | Gardner Road Pumping Station (Site ID 25027) (LAN0058) | NPSWQD011000 | LAN0058 | SO | Storm Discharge at Pumping Station | SD5003071450 | GB112073064430 | Keer - Lower | RIVER KEER | Lune (Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 188.78 | 21 | 99.98%
United Utilities | GARRICK AVENUE CSO | Garrick Avenue CSO | 016892439 | WIR0075 | SO | CSO on Sewer Network | SJ2526089670 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | NORTH WIRRAL (WEST) | Moreton | Commissioned in 2016 - full year data expected | 7.57 | 3 | 100%
United Utilities | GARSTANG RD/GREAT ECCLESTON PS | Garstang Rd, Great Eccleston PS (Site ID 52544) (WYR0051) | 01WYR0051 | WYR0051 | SO | Storm Discharge at Pumping Station | SD4325040650 | GB112072066250 | Wyre - conf R Brock to tidal | RIVER WYER ESTUARY | Lune (Wyre Estuary) Lune (Broadfleet) | Morcambe South | Commissioned in 2016 - full year data expected | 655.69 | 83 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GARSTANG ROAD BRIDGE CSO 333EH | Garstang Road Bridge CSO | 01PRE0034 | PRE0034 | SO | CSO on Sewer Network | SD5327031770 | GB112071065470 | Savick Brook | SAVICK BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 23.27 | 17 | 100%
United Utilities | GARSTANG ROAD/BILSBORROW PS | Garstang Road, Bilsborrow PS | 017280326 | WYR0009 | SO | Storm Discharge at Pumping Station | SD5095039680 | GB112072065790 | New Draught Brook | BACCHUS BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 235 | 29 | 100%
United Utilities | GARSTANG STW | GARSTANG WwTW | 017260046 | 17260046 | ST | Storm Tank at WwTW | SD4788042750 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | N/A | Commissioned in 2020 - full year data expected | 1024.68 | 186 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GASKELL STREET CSO | Gaskell Street CSO | 016982533 | STH0056 | SO | CSO on Sewer Network | SJ5255094630 | GB112069061170 | Sutton Brook | SUTTON BROOK TRIB SANKEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 130.57 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GASWORKS YARD PUMPING STATION | Gas Yard Pumping Station | 01CON0012 | CON0012 | SO | Storm Discharge at Pumping Station | SJ7035066410 | GB112068055460 | Croco | RIVER CROCO | n/a | n/a | Commissioned in 2016 - full year data expected | 196.19 | 57 | 98.29% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GATE STREET CSO | GATE STREET CSO | 01BBN0031 | BBN0031 | SO | CSO on Sewer Network | SD6932028230 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 13 | 29 | 100%
United Utilities | GATEGILL BECK M/H CSO | Gategill Beck M/H Near River Flats CSO | 01EDE0015 | EDE0015 | SO | CSO on Sewer Network | NY3251025320 | GB112075070460 | Glenderamackin (Greta) | GATEGILL BECK | N/A | N/A | Commissioned in 2018 - full year data expected | 175.23 | 56 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | GATHURST LANE SHEVINGTON CSO | Gathurst Lane (Shevington) CSO | 017091492 | WIG0001 | SO | CSO on Sewer Network | SD5401007370 | GB112071065510 | Mearley Brook | TRIB OF PENDLETON BROOK BY SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 56.3 | 49 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GATHURST LANE SHEVINGTON CSO | Gathurst PS | 017091564 | WIG0031 | SO | Storm Discharge at Pumping Station | SD5401007370 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 52.66 | 28 | 100%
United Utilities | GELT ROAD CSO | CSO at Gelt Road | 017680282 | CAR0089 | SO | CSO on Sewer Network | NY5260061100 | GB102076073981 | Irthing DS Crammel Linn Waterfall | BRAMPTON BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | GEORGE ST CSO | George Street CSO | 016983328 | WIG0227 | SO | CSO on Sewer Network | SD6209003800 | GB112069064520 | Hey/Borsdane Brook | DOG POOL BK,TRB OF BORSDANE BK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | GEORGE STREET CSO | George Street CSO | 017580254 | ALL0099 | SO | CSO on Sewer Network | NY2513048150 | GB102075073390 | Wiza Beck | WIZA BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 93.33 | 35 | 100% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | GEORGE STREET CSO 331VJ | GEORGE STREET CSO | 01PRE0077 | PRE0077 | SO | CSO on Sewer Network | SD5488029260 | 176 | #N/A | TRIBUTARY OF RIVER RIBBLE | N/A | N/A | Commissioned in 2018 - full year data expected | 280.57 | 89 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GILCRUX WWTW GILCR | GILCRUX WwTW | 017570069 | 17570069 | ST | Storm Tank at WwTW | NY1110038360 | GB112075073640 | Ellen (lower) | BULLCLOSE BECK | Silloth | Allonby | Commissioned in 2017 - full year data expected | 3334.52 | 180 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GILDERSLEETS LANE CSO 151VM | Gildersleets Lane CSO | 01CRA0005 | CRA0005 | SO | CSO on Sewer Network | SD8089062610 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | RIVER RIBBLE | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | GILFORD PARK CSO (10542) | Gilford Park CSO | 017670037 | CAR0029 | SO | CSO on Sewer Network | NY4138053680 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Commissioned in 2020 - full year data expected | 25.13 | 19 | 100%
United Utilities | GILSLAND (BATH HOUSE) CSO (101VN) | Gilsland (Bath House) CSO | 017680314 | CAR0068 | SO | CSO on Sewer Network | NY6340066530 | GB102076073981 | Irthing DS Crammel Linn Waterfall | RIVER IRTHING | N/A | N/A | Commissioned in 2020 - full year data expected | 10.83 | 12 | 94.62%
United Utilities | GILSLAND WWTW | GILSLAND WwTW | 017670091 | 17670091 | SO | Inlet CSO at WwTW | NY6290066400 | GB102076073981 | Irthing DS Crammel Linn Waterfall | RIVER IRTHING | N/A | N/A | Commissioned in 2019 - full year data expected | 651.12 | 109 | 99.53% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | GINGER FOLD CSO BOL0144 | Ginger Fold CSO | 016993548 | BOL0144 | SO | CSO on Sewer Network | SD7509406798 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | N/A | N/A | Commissioned in 2019 - full year data expected | 362.36 | 106 | 99.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | GISBURN AVENUE CSO 071VO | GISBURN AVENUE CSO | 01BOL0120 | BOL0120 | SO | CSO on Sewer Network | SD6893010900 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 158.73 | 41 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GISBURN WWTW GISBN | GISBURN WwTW | 017160034 | 17160034 | SO | Inlet CSO at WwTW | SD8190049520 | GB112071065612 | Ribble DS Stock Beck | RIVER RIBBLE | n/a | n/a | Commissioned in 2018 - full year data expected | 864.8 | 115 | 99.99% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | GISBURN WWTW GISBN | GISBURN WwTW | 017160034 | 17160034 | ST | Storm Tank at WwTW | SD8190049520 | GB112071065612 | Ribble DS Stock Beck | RIVER RIBBLE | n/a | n/a | Commissioned in 2018 - full year data expected | 320.19 | 30 | 100%
United Utilities | GLASSON PUMPING STATION | Glasson PS | 01ALL0123 | ALL0123 | SO | Storm Discharge at Pumping Station | NY2551060350 | 90 | #N/A | UN-NAMED TRIB SOLWAY FIRTH | Solway | n/a | Commissioned in 2017 - full year data expected | 115.33 | 46 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | GLASSON WWTW | Glasson Wastewater Treatment Works (GLASN) | 017680455 | 17680455 | SO | Inlet CSO at WwTW | NY2607060420 | 90 | #N/A | TRIB SOLWAY FIRTH ESTUARINE WT | Solway | N/A | Commissioned in 2016 - full year data expected | 505.21 | 123 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation
United Utilities | GLASSONBY VILLAGE WWTW | GLASSONBY VILLAGE WwTW | 017680299 | 17680299 | SO | Inlet CSO at WwTW | NY5774439384 | GB102076073820 | Glassonby Beck | GLASSONBY BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | GLAZEBROOK LANE CSO IN FIELD | Glazebrook Lane CSO | 01WAR0040 | WAR0040 | SO | CSO on Sewer Network | SJ7019091940 | GB112069061420 | Glaze | GLAZE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 71.13 | 8 | 98.39%
United Utilities | GLAZEBURY SPS | Ravens Bridge Sewage PS | 016920504 | WAR0024 | SO | Storm Discharge at Pumping Station | SJ6756096090 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | Commissioned in 2020 - full year data expected | 399.15 | 69 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GLAZEBURY STW | GLAZEBURY WwTW | 016920350 | 16920350 | ST | Storm Tank at WwTW | SJ6768095920 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | Commissioned in 2020 - full year data expected | 1705.15 | 138 | 99.16% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GLEASTON CASTLE CSO | Gleaston Castle CSO | 017480365 | LAK0053 | SO | CSO on Sewer Network | SD2607072140 | GB112073071150 | Deep Meadows Beck | GLEASTON BECK | MORECAMBE BAY (LEVEN) | N/A | Commissioned in 2018 - full year data expected | 2858.53 | 129 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GLEBE ROAD PUMPING STATION | Glebe Road PS | 017370148 | LAK0045 | SO | Storm Discharge at Pumping Station | SD3941096350 | GB112073071420 | Leven | WINDERMERE | n/a | n/a | Commissioned in 2017 - full year data expected | 0.83 | 2 | 100%
United Utilities | GLEN HOUSE CSO | GLEN HOUSE CSO | 01ALL0016 | ALL0016 | SO | CSO on Sewer Network | NY0561028770 | GB112075070540 | Marron | UNNAMED TRIB OF RIVER MARRON | N/A | N/A | Commissioned in 2018 - full year data expected | 225.13 | 55 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GLENBROOK RD EXTER RD CSO 281VU | Glenbrook Road/Dexter Road CSO | 01MAN0125 | MAN0125 | SO | CSO on Sewer Network | SD8415004420 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2018 - full year data expected | 6.53 | 23 | 98%
United Utilities | GLENCROFT PUMPING STATION | Glencroft PS | 017091518 | CHR0028 | SO | Storm Discharge at Pumping Station | SD5500019000 | GB112070064861 | Yarrow Culbeck Brook to tidal | RANSNAP BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | GLENRIDDING WWTW GLNRI | GLENRIDDING WwTW | 017680367 | 17680367 | SO | Inlet CSO at WwTW | NY3845016830 | GB102076070740 | Glenridding Beck | GLENRIDDING BECK | N/A | N/A | Commissioned in 2016 - full year data expected | 83.74 | 54 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GLOSSOP STW (SPS) | GLOSSOP WwTW | 016940172 | 16940172 | ST | Storm Tank at WwTW | SK0058094910 | GB112069061050 | Etherow (Glossop Brook to Goyt) | TRIB RIVER ETHEROW | N/A | N/A | Commissioned in 2020 - full year data expected | 2978.67 | 191 | 99.71% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GLOUCESTER ST CSO | Gloucester street CSO | 016982786 | WIG0207 | SO | CSO on Sewer Network | SD6686003290 | GB112069060810 | Bedford Brook | COLLIER BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1134.14 | 99 | 94.25% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GLOUCESTER STREET | Gloucester Street CSO | 01STH0054 | STH0054 | SO | CSO on Sewer Network | SJ5246094970 | GB112069061180 | Sankey Brook (Hardshaw Brook to Rainford Brook | SANKEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | GLYNRENE DRIVE CSO | Glynrene Drive CSO | EPRSB3397WJ | SAL0114 | SO | CSO on Sewer Network | SD7598002460 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB OF KEMPNOUGH BROOK VI SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.57 | 1 | 100%
United Utilities | GOLDEN HILL LANE CSO | GOLDEN HILL LANE CSO | 01SRI0022 | SRI0022 | SO | CSO on Sewer Network | SD5292022820 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 55.67 | 27 | 100%
United Utilities | GOLF ROAD PUMPING STATION | Golf Road PS | 016892329 | TRA0045 | SO | Storm Discharge at Pumping Station | SJ7778087790 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 179.6 | 59 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GORSE ST COMBINED SEWER OVERFLOW | Gorse Street CSO | NPSWQD010750 | BBN0087 | SO | CSO on Sewer Network | SD6988328677 | GB112071065310 | Blakewater | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | GORSEY LANE DANS RD CSO 201V6 | Gorsey Lane/Dan's Road | 01HAL0042 | HAL0042 | SO | CSO on Sewer Network | SJ5395085223 | 170 | #N/A | RIVER MERSEY VIA SWS | N/A | N/A | Commissioned in 2018 - full year data expected | 234.53 | 98 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GORTON ROAD (LIGHTING TOWER) | Gorton Road CSO | NPSWQD010710 | MAN0199 | SO | CSO on Sewer Network | SJ8604097020 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | BLACK BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 6.51 | 11 | 99.98%
United Utilities | GOSFORTH WWTW | GOSFORTH WwTW | 017470040 | 17470040 | ST | Storm Tank at WwTW | NY0782002750 | GB112074070090 | Bleng | HARE BECK | N/A | Seascale | Commissioned in 2016 - full year data expected | 643.86 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GOUGH AVENUE/SANDY LANE WEST CSO | Junction Sandy Lane/ Bough Avenue CSO | 01WAR0051 | WAR0051 | SO | CSO on Sewer Network | SJ6019090830 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | MILL BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 112.8 | 20 | 100%
United Utilities | GOWER STREET CSO 50126 | Gower Street CSO | 017081268 | WIG0202 | SO | CSO on Sewer Network | SD5712005210 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 48.59 | 32 | 99.27%
United Utilities | GOWER STREET CSO 50126 | Gower Street/Kings Dock CSO | 017081268 | LIV0030 | SO | CSO on Sewer Network | SD5712005210 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | N/A | Commissioned in 2018 - full year data expected | 0.34 | 2 | 100%
United Utilities | GOYT SIDE SPS | Goyt Side PS | 016982416 | PEA0075 | SO | Storm Discharge at Pumping Station | SK0015085100 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | 43.05 | 29 | 100%
United Utilities | GRANGE BRIDGE PS GNGBO ALL0062 | Grange Bridge (200mtrs downstream) | 017570113 | ALL0062 | SO | Storm Discharge at Pumping Station | NY2550017600 | GB112075070410 | Derwent - Stonethwaite Beck to conf Greta | RIVER DERWENT | N/A | N/A | Commissioned in 2016 - full year data expected | 414.45 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | GRANGE FARM COMBINED SEWER OVERFLOW | Grange Farm CSO | 017580318 | ALL0020 | SO | CSO on Sewer Network | NY1096041640 | GB112075073660 | Crookhurst Beck | TRIBUTARY OF PATTEN BECK | SILLOTH | Allonby | Commissioned in 2016 - full year data expected | 31.63 | 20 | 94%
United Utilities | GRANGE LANE CSO | GRANGE LANE CSO | 01HYN0033 | HYN0033 | SO | CSO on Sewer Network | SD7623028250 | GB112071065040 | Hyndburn | BROAD OAK WATER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | GRANGE OVER SANDS WWTW GRNGS | GRANGE-OVER-SANDS WwTW | 017370128 | 17370128 | SO | Inlet CSO at WwTW | SD3926075060 | 184 | #N/A | KENT CHANNEL MORECAMBE ESTUARY | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 141.28 | 71 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GRANGE PUMPING STATION | Grange PS | 017380194 | LAK0074 | SO | Storm Discharge at Pumping Station | SD4125078160 | GB531207312000 | KENT | KENT ESTUARY | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 144.4 | 38 | 99.16%
United Utilities | GRANGE VALLEY | Grange Valley | 01STH0069 | STH0069 | SO | Storm Discharge at Pumping Station | SJ5585096140 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | FRESHWATER STTEAM | N/A | N/A | Commissioned in 2019 - full year data expected | 1.17 | 9 | 100%
United Utilities | GRASMERE WWTW | Grasmere Waste Water Treatment Works | 017370027 | 17370027 | SO | Inlet CSO at WwTW | NY3392006840 | GB112073071140 | Rothay | GRASMERE LAKE | n/a | n/a | Commissioned in 2018 - full year data expected | 1347.88 | 90 | 99.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GRASSCROFT SEWAGE SCHEME | Armit Road (Grasscroft) CSO | 016950639 | OLD0107 | SO | CSO on Sewer Network | SD9802003930 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 186.27 | 17 | 100%
United Utilities | GRASSENDALE COMBINED SEWER OVERFLOW | Grassendale CSO | 016930985 | LIV0053 | SO | CSO on Sewer Network | SJ3853084780 | 167 | #N/A | MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 15.02 | 15 | 100%
United Utilities | GRAVING DOCK PUMPING STATION | Graving Dock Pumping Station (Site ID 04525) (BRW0100) | 017480340 | BRW0100 | SO | Storm Discharge at Pumping Station | SD1889069320 | 344 | #N/A | THE WALNEY CHANNEL | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 31.54 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GREASBY ROAD/CORTSWAY CSO 511WQ | Greasby Road/ Cortsway Combined Sewer Overflow (Site ID 511WQ) (WIR0085) | 01WIR0085 | WIR0085 | SO | CSO on Sewer Network | SJ2634088090 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 19.13 | 11 | 100%
United Utilities | GREAT ASBY WWTW | GREAT ASBY WwTW | 017680364 | 17680364 | SO | Inlet CSO at WwTW | NY6859013710 | GB102076070630 | Hoff Beck (upper) | ASBY BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 432.7 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREAT BOLTON STREET CSO | Great Bolton Street CSO | 01BBN0025 | BBN0025 | SO | CSO on Sewer Network | SD6806827642 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 94.17%
United Utilities | GREAT BRIDGEWATER ST CSO (281WI) | Great Bridgewater Street CSO | 016982707 | MAN0252 | SO | CSO on Sewer Network | SJ8381097460 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.03 | 1 | 100%
United Utilities | GREAT BROUGHTON WWTW | GREAT BROUGHTON WwTW | 017570041 | 17570041 | ST | Storm Tank at WwTW | NY0706030500 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | GREAT BROUGHTON WWTW | GREAT BROUGHTON WwTW | 017570041 | 17570041 | SO | Inlet CSO at WwTW | NY0706030500 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | GREAT CLOWES CSO 37048 SAL0080 | Great Clowes Street/Sussex Street CSO | 016993788 | SAL0080 | SO | CSO on Sewer Network | SJ8290099370 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2017 - full year data expected | 375.76 | 85 | 95.85% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREAT CORBY SYPHON CSO (10C88) | Great Corby Syphon CSO | 01CAR0018 | CAR0018 | SO | CSO on Sewer Network | NY4678055160 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Commissioned in 2017 - full year data expected | 0.17 | 1 | 100%
United Utilities | GREAT HARWOOD (HYNBURN RD)CSO 22017 | Great Harwood (Hyndbunr Rd) CSO | 017160127 | HYN0009 | SO | CSO on Sewer Network | SD7470032330 | GB112071065070 | Hyndburn Brook - Lower | HYNDBURN BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 80.81 | 55 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | GREAT ORTON WWTW (GRORT) | GREAT ORTON WwTW | 017670128 | 17670128 | ST | Storm Tank at WwTW | NY3332054490 | GB102076073950 | Powburgh Beck | ROUGHTON BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 1569.91 | 156 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | GREAT SALKELD WWTW GRSAL | GREAT SALKELD WwTW | 017670061 | 17670061 | SO | Inlet CSO at WwTW | NY5569036430 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | n/a | n/a | Commissioned in 2017 - full year data expected | 228.16 | 86 | 99.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GREAT UNDERBANK CSO 43200 STK0039 | Great Underbank CSO | 016940449 | STK0039 | SO | CSO on Sewer Network | SJ8947090460 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | CLVRT SECTION OF RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 78.12 | 44 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREAVE CLOUGH DRIVE CSO | Greave Clough Drive CSO | 016982934 | ROS0076 | SO | CSO on Sewer Network | SD8749023220 | GB112069064660 | Irwell (Source to Whitewell Brook) | GREAVE CLOUGH VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | GREEN DRAGON HOTEL CSO 481EC | GREEN DRAGON HOTEL CSO | 01WAR0067 | WAR0067 | SO | CSO on Sewer Network | SJ7021088750 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | N/A | N/A | Commissioned in 2018 - full year data expected | 250.97 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREEN LANE LYNDHURST AVE CSO | Green Lane/Lyndhurst Avenue CSO | 016993675 | TAM0049 | SO | CSO on Sewer Network | SD9376000210 | GB112069061151 | Medlock (Source to Lumb Brook) | SMALLSHAW BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 5.97 | 8 | 100%
United Utilities | GREEN ROW SILLOTH | Greenrow (Silloth) PS | 017580260 | ALL0109 | SO | Storm Discharge at Pumping Station | NY1124052680 | 90 | #N/A | TRIB GREAT GUTTER | Solway and Silloth | Silloth | Commissioned in 2017 - full year data expected | 5.97 | 5 | 100%
United Utilities | GREENBANK LANE CSO NORTHWICH | Greenbank Lane CSO Northwich | 016892403 | VRY0073 | SO | CSO on Sewer Network | SJ6510072320 | GB112068060460 | Weaver (Marbury Brook to Dane) | THE RIVER WEAVER | N/A | N/A | Commissioned in 2017 - full year data expected | 131.27 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREENBANK LANE CSO NORTHWICH | Greenbank Road | 016892403 | ROC0127 | SO | CSO on Sewer Network | SJ6510072320 | GB112068060460 | Weaver (Marbury Brook to Dane) | THE RIVER WEAVER | N/A | N/A | Commissioned in 2017 - full year data expected | 0 | 0 | 99.98%
United Utilities | GREENBANK ROAD/ROSSALL ROAD CSO | Greenbank Road pumping station (Site ID 51001) (WIR0092) | EPRQB3593VE | WIR0092 | SO | Storm Discharge at Pumping Station | SD8998014560 | GB112069064720 | Roch (Source to Spodden) | FOXHOLES BROOK | N/A | N/A | Commissioned in 2016 - full year data expected | 0.15 | 1 | 99.94%
United Utilities | GREENFIELD CHEW VALLEY ROAD CSO | Greenfield Chew Valley Combined Sewer Overflow | 01OLD0059 | OLD0059 | SO | CSO on Sewer Network | SD9935004350 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 630.63 | 37 | 63.6% | Comms failure / issue | N/A - Ongoing investigation |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | GREENGATE COMBINED SEWER OVERFLOW | Greengate CSO | 016982738 | OLD0128 | SO | CSO on Sewer Network | SD8847004800 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 70.14 | 36 | 99.99%
United Utilities | GREENLEACH LANE CSO | Greenleach Lane CSO | 016993659 | SAL0125 | SO | CSO on Sewer Network | SD7520001310 | GB112069061430 | Folly Brook and Salteye Brook. | KEMPNOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 52.77 | 11 | 100%
United Utilities | GREENODD PUMPING STATION | Greenodd Sewage Pumping Station (Site ID 398CS, GREEN ) (LAK0109) | EPRFP3828XR | LAK0109 | SO | Storm Discharge at Pumping Station | SD3148082410 | 181 | #N/A | RIVER LEVEN | MORECAMBE BAY (LEVEN) | N/A | Commissioned in 2018 - full year data expected | 675.51 | 60 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GREENWOOD AVE PLATT AVE CSO 441XE | Greenwood Avenue/Platt Avenue CSO | 01TAM0051 | TAM0051 | SO | CSO on Sewer Network | SD9423000520 | GB112069061151 | Medlock (Source to Lumb Brook) | SMALLSHAW BROOK VIA SWS | N/A | N/A | Commissioned in 2018 - full year data expected | 1.1 | 1 | 100%
United Utilities | GREENWOOD AVENUE CSO | Greenwood Avenue CSO | EPRAB3991EH | WIG0243 | SO | CSO on Sewer Network | SD5620005774 | GB112070064820 | Douglas - Lower | CLOSE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 572.43 | 109 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREETY GATE PUMPING STATION | Gregson Lane Area CSO | 017480364 | SRI0014 | SO | CSO on Sewer Network | SD2030186811 | 187 | #N/A | DUDDON ESTUARY | n/a | n/a | Commissioned in 2019 - full year data expected | 323.2 | 106 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GREETY GATE PUMPING STATION | Greety Gate PS | 017480364 | LAK0098 | SO | Storm Discharge at Pumping Station | SD2030186811 | 187 | #N/A | DUDDON ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 272.47 | 39 | 97.04% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | GREYHOUND INN CSO 021WR | GREY HOUND INN CSO | 01ALL0015 | ALL0015 | SO | CSO on Sewer Network | NY1833039250 | GB112075073640 | Ellen (lower) | BOTHEL BECK | N/A | N/A | Commissioned in 2018 - full year data expected | 28.73 | 32 | 99.75%
United Utilities | GREYSOUTHEN WWTW | GREYSOUTHEN WwTW | 017570043 | 17570043 | SO | Inlet CSO at WwTW | NY0716030400 | GB112075070520 | Derwent - conf Cocker to tidal | TRIB RIVER DERWENT | N/A | N/A | Commissioned in 2020 - full year data expected | 810.57 | 107 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREYSTOKE PS | Greystoke Wastewater Process PS | 017670163 | EDE0059 | SO | Storm Discharge at Pumping Station | NY4356030770 | GB102076073992 | Petteril u/s M6 | RIVER NORTH PETTERIL | N/A | N/A | Commissioned in 2019 - full year data expected | 2517.06 | 134 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GREYSTOKE WWTW | GREYSTOKE WwTW | 017670101 | 17670101 | SO | Inlet CSO at WwTW | NY4459031190 | GB102076073992 | Petteril u/s M6 | RIVER PETTERIL | N/A | N/A | Commissioned in 2019 - full year data expected | 267.49 | 18 | 97.07%
United Utilities | GRIMSARGH CSO 333LG | Grimsargh CSO | 01PRE0061 | PRE0061 | SO | CSO on Sewer Network | SD5896034240 | GB112071065500 | Ribble - conf Calder to tidal | TRIB TUN BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.13 | 1 | 98.34%
United Utilities | GRIMSHAW PARK CSO | Grimshaw Park CSO | 01BBN0037 | BBN0037 | SO | CSO on Sewer Network | SD6854027100 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | GRIMSHAW STREET CSO | Grimshaw Street Combined Sewer Overflow (Site ID 05033) (BBN0107) | 017190805 | BBN0107 | SO | CSO on Sewer Network | SD6978021120 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 18.81 | 26 | 99.99%
United Utilities | GRINDLETON WWTW | GRINDLETON WwTW | 017160035 | 17160035 | ST | Storm Tank at WwTW | SD7569044770 | GB112071065612 | Ribble DS Stock Beck | RIVER RIBBLE/WEST CLOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1505.3 | 130 | 99.56% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GRISEDALE CLOSE CSO | Grisedale Close CSO | 017480430 | COP0042 | SO | CSO on Sewer Network | NX9808015940 | 356 | #N/A | POW BECK | N/A | St Bees | Commissioned in 2016 - full year data expected | 10.53 | 21 | 98.24%
United Utilities | GROVE ROAD CSO | Grove Road CSO | 016993678 | TAM0096 | SO | CSO on Sewer Network | SJ9748099950 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 330.17 | 85 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | GYNN SQUARE | Gynn Square CSO | 017180573 | BPL0035 | SO | CSO on Sewer Network | SD3060037800 | 349 | #N/A | IRISH SEA | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HACKEN WORKS CSO | West of Hacken Works (Syphon) CSO | 016993558 | BOL0013 | SO | CSO on Sewer Network | SD7334007810 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | N/A | N/A | Commissioned in 2019 - full year data expected | 922.45 | 139 | 99.63% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | HAG END BROW CSO | Hag End Brow CSO | 016993783 | BOL0111 | SO | CSO on Sewer Network | SD7327008350 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Commissioned in 2019 - full year data expected | 25.51 | 48 | 91.65% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HAGG LANE MIDLAND TERRACE PS | Hagg Lane (Midland Terrace) PS | 01LAN0059 | LAN0059 | SO | Storm Discharge at Pumping Station | SD4966071170 | GB112073064430 | Keer - Lower | RIVER KEER | Morcambe Bay East | Morcambe North | Commissioned in 2016 - full year data expected | 43.18 | 13 | 99.61%
United Utilities | HALE ROAD / DINNER LANE CSO | Everite Road Combined Sewer Overflow (Site ID 20046) (HAL0004) | 016982704 | HAL0004 | SO | CSO on Sewer Network | SJ4633082310 | 167 | #N/A | LADY POOL | N/A | N/A | Commissioned in 2019 - full year data expected | 125.84 | 62 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HALE ROAD / DINNER LANE CSO | Hale Road/Dinner Lane | 016982704 | HAL0123 | SO | CSO on Sewer Network | SJ4633082310 | 167 | #N/A | LADY POOL | n/a | n/a | Commissioned in 2019 - full year data expected | 33.23 | 19 | 97% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HALE STORM TANKS & PUMPING STATION | Hale Storm Tanks and WwPPS | 016940005 | TRA0102 | SO | Storm Discharge at Pumping Station | SJ7729085590 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | N/A | N/A | Commissioned in 2020 - full year data expected | 90.89 | 20 | 21.05% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | HALE STORM TANKS & PUMPING STATION | Hale Storm Tanks and WwPPS | 016940005 | TRA0102 | ST | Storm Discharge at Pumping Station | SJ7729085590 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | HALE VILLAGE PUMPING STATION | Hale Village PS | 016920551 | HAL0093 | SO | Storm Discharge at Pumping Station | SJ4747082910 | 167 | #N/A | RAM'S BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 232.24 | 62 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HALE VILLAGE PUMPING STATION | Halewood Pumping Station (HALEW) (HAL0134) | 016920551 | HAL0134 | SO | Storm Discharge at Pumping Station | SJ4747082910 | 167 | #N/A | RAM'S BROOK | n/a | n/a | Commissioned in 2019 - full year data expected | 2.9 | 3 | 100%
United Utilities | HALL COPPICE SSO | Hall Coppice CSO | 016950415 | BOL0057 | SO | CSO on Sewer Network | SD7085014340 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HALL I TH WOOD CSO 071XP | HALL i' th WOOD CSO | 01BOL0071 | BOL0071 | SO | CSO on Sewer Network | SD7222011410 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 0.03 | 1 | 100%
United Utilities | HALL LANE | Hall Lane Combined Sewer Overflow (Site ID 07035) (BOL0145) | 01BOL0145 | BOL0145 | SO | CSO on Sewer Network | SD7422006980 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | n/a | n/a | Commissioned in 2017 - full year data expected | 19.35 | 28 | 100%
United Utilities | HALL MOSS LANE PS | Hall Moss Lane PS | 016992842 | STK0144 | SO | Storm Discharge at Pumping Station | SJ8801083850 | GB112069061360 | Dean (Bollington to Bollin) | SPATH BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HALL NOOK COMBINED SEWER OVERFLOW | Hall Nook CSO (481XO) (WAR0007) | 01WAR0007 | WAR0007 | SO | CSO on Sewer Network | SJ5666487360 | 170 | #N/A | PENKETH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 223.83 | 75 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HALLS ROAD CSO (411XQ) | Halls Road CSO | 016810193 | STA0006 | SO | CSO on Sewer Network | SJ8858058380 | GB112068055360 | Biddulph Brook | GILLOW SHAW, TRIB BIDDULPH BRK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.27 | 1 | 100% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HALSBURY STREET CSO 331XR | Halsbury Street CSO | 01PRE0072 | PRE0072 | SO | CSO on Sewer Network | SD5461028960 | 176 | #N/A | SWILL BROOK CLVRT RIVER RIBBLE | N/A | N/A | Commissioned in 2018 - full year data expected | 0.87 | 5 | 93.97%
United Utilities | HALTON BROW CSO 203EF | Halton Brow CSO | 01HAL0062 | HAL0062 | SO | CSO on Sewer Network | SJ5315083431 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 120.57 | 91 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HALTON EAST SEWAGE PUMPING STATION | Halton East sewage pumping station (Site ID HALTN) (LAN0060 | 01LAN0060 | LAN0060 | SO | Storm Discharge at Pumping Station | SD5030064700 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 156.43 | 73 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | HALTON EAST STW | HALTON EAST WwTW | 017270002 | 17270002 | ST | Storm Tank at WwTW | SD5053064611 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 40.59 | 21 | 100%
United Utilities | HALTON WEST PUMPING STATION HLTWE | Halton West SPS | 017280287 | LAN0097 | SO | Storm Discharge at Pumping Station | SD4998064660 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 46.07 | 21 | 100%
United Utilities | HAMMERTONSTREET/STANLEY STREET CSO | Hammerton Street/Stanley Street CSO | 01ROS0016 | ROS0016 | SO | CSO on Sewer Network | SD8669023560 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HAMPDEN ROAD CSO 091XV | Hampden Road CSO | 016993787 | BRY0041 | SO | CSO on Sewer Network | SD8191003930 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH VIA CLVRT | n/a | n/a | Commissioned in 2018 - full year data expected | 4.93 | 8 | 100%
United Utilities | HAMPTON ST/ORDSALL LANE | Hampton Street/Ordsall Lane | 01SAL0183 | SAL0183 | SO | CSO on Sewer Network | SJ8268098020 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HANKINSON WAY CSO | Hankinson Way CSO | 016982903 | SAL0185 | SO | CSO on Sewer Network | SJ7961097700 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 2.43 | 8 | 100%
United Utilities | HANOVER STREET CSO | HANOVER STREET CSO | 01TAM0111 | TAM0111 | SO | CSO on Sewer Network | SJ9590098820 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | CULVERT TO RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HANOVER STREET CSO | Hanover Street/Long Millgate CSO | 01MAN0158 | MAN0158 | SO | CSO on Sewer Network | SJ8405098970 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.07 | 2 | 100%
United Utilities | HAPATIA STREET CSO 074EA | Hypatia Street CSO | 016983219 | BOL0107 | SO | CSO on Sewer Network | SD7283009350 | GB112069064530 | Tonge | RIVER TONGE | n/a | n/a | Commissioned in 2018 - full year data expected | 86.66 | 51 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | HAPSFORD SPS | Hapsford PS | 016810286 | CHE0015 | SO | Storm Discharge at Pumping Station | SJ4713074550 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | HORNSMILL BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 54.51 | 21 | 100%
United Utilities | HARBORD ROAD PS 99047 | Harbord Road Sewage Pumping Station (Site ID 99047 ) (SEF0103) | 016931010 | SEF0103 | SO | CSO on Sewer Network | SJ3080097840 | 348 | #N/A | LIVERPOOL BAY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 20.14 | 22 | 100%
United Utilities | HARBOUR YARD PUMPING STATION | Harbour Yard Pumping Station (Site ID 04524) (BRW0101) | 017480339 | BRW0101 | SO | Storm Discharge at Pumping Station | SD1944067720 | 340 | #N/A | THE WALNEY CHANNEL | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 23.44 | 55 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HARDWICK ROADCSO | Hardwick Street CSO | 01HAL0008 | HAL0008 | SO | CSO on Sewer Network | SJ5253083240 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2019 - full year data expected | 188.17 | 54 | 98.55% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HARESFINCH ROAD | Haresfinch Road CSO | 01STH0051 | STH0051 | SO | CSO on Sewer Network | SJ5162096220 | GB112069061240 | Rainford Brook | RAINFORD BROOK | N/A | N/A | October 2021 | 0 | 0 | 99.99%
United Utilities | HARRINGTON AVENUE CSO | Harrington Avenue CSO | 016892362 | WIR0091 | SO | CSO on Sewer Network | SJ2237088980 | GB112068060530 | The Birket including Arrowe Brook and Fender | TRIB CARR DRAIN (TO R. BIRKET) | North Wirral East | Wallasey | Commissioned in 2016 - full year data expected | 127.83 | 41 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HARRISON ROAD WAGON AND HORSE CSO | Harrisons Road Wagon & Horses CSO | 017091496 | CHR0061 | SO | CSO on Sewer Network | SD6017012550 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 97.39 | 56 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HARRISON STREET CSO | Harrison Street CSO | 016993466 | HAL0040 | SO | CSO on Sewer Network | SJ4895084630 | 167 | #N/A | DITTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 408.83 | 72 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HARROWSIDE PUMPING STATION | Harrowside Pumping Station | 017180568 | BPL0003 | SO | Storm Discharge at Pumping Station | SD3063132517 | 350 | #N/A | IRISH SEA | Ribble | Blackpool North, Blackpool Central, and Blackpool South | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | HARTLEY LANE CSO | Hartley Lane | EPRSB3396RE | ROC0066 | SO | CSO on Sewer Network | SD8956011440 | GB112069064600 | Roch (Spodden to Irwell) | TRIB OF SUDDON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 99.25 | 60 | 99.91% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HARTSHEAD CLOSE/MANSHAW ROAD CSO | HARTSHEAD CLOSE / MANSHAW ROAD CSO | 01MAN0203 | MAN0203 | SO | CSO on Sewer Network | SJ9013897264 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CULVERTED SECTION MOSS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 102.2 | 10 | 100%
United Utilities | HASLAM PARK NORTH & SOUTH CSO | Haslam Park North and South Combined Sewer Overflow (Site ID 33026) (PRE0090) | 017190870 | PRE0090 | SO | CSO on Sewer Network | SD5140031171 | GB112071065470 | Savick Brook | SAVICK BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 385.6 | 31 | 100%
United Utilities | HASLAM PARK NORTH & SOUTH CSO | Haslam Park North and South Combined Sewer Overflow (Site ID 33026) (PRE0090) | 017190870 | PRE0090 | SO | CSO on Sewer Network | SD5140031171 | GB112071065470 | Savick Brook | SAVICK BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | HASSALL RD CREWE RD CSO 131QJ | HASSALL ROAD / CREWE ROAD CSO | 01CON0022 | CON0022 | SO | CSO on Sewer Network | SJ7878155326 | GB112068074630 | Valley Brook (Source to Englesea Brook) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | HASSALL ROAD CSO 131X8 | HASSALL ROAD CSO | 01CON0046 | CON0046 | SO | CSO on Sewer Network | SJ7621059540 | GB112068055410 | Wheelock (Source to Kidsgrove Stream) | RIVER WHEELOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 353.47 | 53 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HATHERSHAW CSO | Hathershaw Playing Field | 016952063 | OLD0109 | SO | CSO on Sewer Network | SD9288001150 | GB112069061151 | Medlock (Source to Lumb Brook) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 165.37 | 18 | 100%
United Utilities | HATLEY LANE COMBINED SEWER OVERFLOW | Hatley Lane | 016881726 | VRY0139 | SO | CSO on Sewer Network | SJ5070077310 | GB112068060500 | Weaver (Dane to Frodsham) | FRODSHAM MARSH DITCH | N/A | N/A | Commissioned in 2019 - full year data expected | 5.73 | 11 | 100%
United Utilities | HAVERIGG PUMPING STATION | Haverigg PS | 017480403 | BRW0005 | SO | Storm Discharge at Pumping Station | SD1608078760 | GB641211172000 | Duddon Sands | HAVERIGG POOL | Duddon | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 560.63 | 48 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HAWCOAT LANE/HARTLAND ROAD CSO | Hawcoat Lane/Hartland Road CSO | 01BRW0031 | BRW0031 | SO | CSO on Sewer Network | SD2194069336 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | HAWCOAT LANE/THORNCLIFFE ROAD CSO | Hawcoat Lane/Thorncliffe Road CSO | 01BRW0032 | BRW0032 | SO | CSO on Sewer Network | SD2194069337 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | HAWKSHEAD PUMPING STATION | Hawkshead Pumping Station (Site ID HWKSH) (LAK0107) | 017380284 | LAK0107 | SO | Storm Discharge at Pumping Station | SD3552197931 | GB112073071400 | Cunsey Beck/Black Beck | BLACK BECK | n/a | n/a | Commissioned in 2017 - full year data expected | 1371.86 | 67 | 99.24% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HAWTHORN AVENUE/RAILWAY BRIDGE CSO | Hawthorn Avenue/Railway Bridge CSO | 017570201 | ALL0032 | SO | CSO on Sewer Network | NY0431036400 | GB112075073640 | Ellen (lower) | GILL BECK | SILLOTH | Allonby South | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | HAWTHORN CRESCENT CSO | Hawthorn Crescent CSO | NPSWQD010099 | PRE0122 | SO | CSO on Sewer Network | SD4948029980 | 176 | #N/A | RIVER RIBBLE | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 3.37 | 11 | 100%
United Utilities | HAWTHORN LANE CSO | Hawthorn Lane | 016982619 | MAC0155 | SO | CSO on Sewer Network | SJ8469081460 | GB112069061320 | Bollin (Source to Dean) | CLVRT'D TRIB OF RIVER BOLLIN | N/A | N/A | Commissioned in 2019 - full year data expected | 5.87 | 14 | 100%
United Utilities | HAWTHORN ROAD CSO 451YJ | Hawthorn Road CSO | 01TRA0013 | TRA0013 | SO | CSO on Sewer Network | SJ7748087990 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0.1 | 2 | 100%
United Utilities | HAYES CASTLE FARM CSO (02628) | Rear of Hayes Castle Farm CSO | 017580390 | COP0096 | SO | CSO on Sewer Network | NY0006022370 | GB112074070040 | Lowca Beck | DISTINGTON BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 360.5 | 66 | 88.38% | Sensor failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | HAYFIELD WASTEWATER TREATMENT WORKS | HAYFIELD WwTW | 016940174 | 16940174 | ST | Storm Tank at WwTW | SK0266087140 | GB112069060970 | Sett | RIVER SETT | N/A | N/A | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | Investigation now complete, remedial work due
United Utilities | HAYTON PUMPING STATION | Hayton PS | 017680324 | CAR0079 | SO | Storm Discharge at Pumping Station | NY5048057930 | GB102076073981 | Irthing DS Crammel Linn Waterfall | BYE GILL | n/a | n/a | Commissioned in 2018 - full year data expected | 0.02 | 3 | 100%
United Utilities | HAYTON STW | HAYTON WwTW | 017570084 | 17570084 | ST | Storm Tank at WwTW | NY1076041830 | GB112075073660 | Crookhurst Beck | PATTEN BECK | SILLOTH | Allonby | Commissioned in 2016 - full year data expected | 587.45 | 74 | 99.34% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | HAZEL GROVE STW | Hazel Grove WwTW | 016940175 | 16940175 | ST | Storm Tank at WwTW | SJ9312089440 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | HAZELWOOD ROAD CSO 435GY | Hazelwood Road combined sewer overflow (435GY) (STK0094) | 016982761 | STK0094 | SO | CSO on Sewer Network | SJ9269087210 | GB112069060950 | Poise Brook | POISE BROOK TRIB RVR GOYT | n/a | n/a | Commissioned in 2018 - full year data expected | 47.2 | 52 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HEADS NOOK PUMPING STATION | Heads Nook Pumping Station (10507) (CAR0080) | 017680325 | CAR0080 | SO | Storm Discharge at Pumping Station | NY4961055290 | GB102076073900 | Trout Beck (Cairn Beck) | TRIB TROUT BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.65%
United Utilities | HEADS NOOK WWTW | HEADS NOOK WwTW | 017670062 | 17670062 | SO | Inlet CSO at WwTW | NY4903055070 | GB102076073870 | Cairn Beck | CAIRN BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 262.34 | 87 | 100% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation
United Utilities | HEAPEY ROAD CSO 121YP | Heapey CSO | 01CHR0013 | CHR0013 | SO | CSO on Sewer Network | SD6001018920 | GB112070064951 | Yarrow US Big Lodge Water | BLACK BROOK, TRIB OF R YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 0.07 | 1 | 100%
United Utilities | HEATON BRIDGE CSO BOLTON | Heaton Bridge CSO | 016982883 | BOL0230 | SO | CSO on Sewer Network | SD6791008840 | GB112069064540 | Middle Brook | MIDDLE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 8.4 | 21 | 100%
United Utilities | HEATON MOOR CSO 431YX | Heaton Moor CSO | 016982679 | STK0119 | SO | CSO on Sewer Network | SJ8596090050 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 28.13 | 11 | 100%
United Utilities | HELLIFIELD STW | HELLIFIELD WwTW | 017160036 | 17160036 | SO | Inlet CSO at WwTW | SD8475856288 | GB112071065613 | Ribble (Long Preston to Stock Beck) | HELLIFIELD (PAN) BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 1812.53 | 211 | 91.88% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HELLIFIELD STW | HELLIFIELD WwTW | 017160036 | 17160036 | ST | Storm Tank at WwTW | SD8475856288 | GB112071065613 | Ribble (Long Preston to Stock Beck) | HELLIFIELD (PAN) BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 91.88%
United Utilities | HELMSHORE CARAVAN PARK CSO | Helmshore Caravan Park combined sewer overflow | 01ROS0036 | ROS0036 | SO | CSO on Sewer Network | SD7784022060 | GB112069064650 | Ogden | SWINNEL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 180.22 | 63 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HELSBY WWTW | HELSBY WwTW | 016810187 | 16810187 | ST | Storm Tank at WwTW | SJ4815275072 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | HORNSMILL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 115.33 | 12 | 99.58%
United Utilities | HELSBY WWTW | HELSBY WwTW | 016810187 | 16810187 | SO | Inlet CSO at WwTW | SJ4815275072 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | HORNSMILL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 79.84 | 11 | 99.57%
United Utilities | HENDHAM VALE CSO | Hendham Vale CSO | 016993691 | MAN0072 | SO | CSO on Sewer Network | SD8514000960 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 91.55%
United Utilities | HENNEL LANE CSO | Hennel Lane CSO | 017180616 | SRI0011 | SO | CSO on Sewer Network | SD5518027980 | 175 | #N/A | RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 531 | 59 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HESKET NEWMARKET PUMPING STATION | Hesket Newmarket Pumping Station (02509) (ALL0119) | 017680308 | ALL0119 | SO | Storm Discharge at Pumping Station | NY3416038780 | GB102076073730 | Caldew (Hesket Newmarket) | RIVER CALDEW | n/a | n/a | Commissioned in 2018 - full year data expected | 72.63 | 30 | 100%
United Utilities | HESKETH BANK WWTW HSKBK | HESKETH BANK WwTW | 017030023 | 17030023 | ST | Storm Tank at WwTW | SD4562023980 | GB531207112400 | RIBBLE | DOUGLAS ESTUARY | Ribble | n/a | Commissioned in 2017 - full year data expected | 143.62 | 16 | 99.94%
United Utilities | HESKETH LANE CSO | HESKETH LANE CSO | 01WLN0019 | WLN0019 | SO | CSO on Sewer Network | SD4569021050 | 175 | #N/A | RIVER DOUGLAS | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 20.7 | 20 | 100%
United Utilities | HEST BANK PUMPING STATION | Hest Bank PS | 017290499 | LAN0120 | SO | Storm Discharge at Pumping Station | SD4684066860 | 185 | #N/A | HATLEX BECK | Morcambe Bay East | Morcambe North | Commissioned in 2017 - full year data expected | 324.38 | 36 | 99.99%
United Utilities | HEVERSHAM SEWAGE PUMPING STATION | Heversham Sewage PS | 01LAK0055 | LAK0055 | SO | Storm Discharge at Pumping Station | SD4864083090 | GB112073071070 | Bela | MARSH DRAIN | N/A | N/A | Commissioned in 2018 - full year data expected | 714.12 | 74 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HEWLETT AVENUE CSO | Hewlett Avenue CSO | NPSWQD010698 | CHR0011 | SO | CSO on Sewer Network | SD5590014090 | GB112070064952 | Yarrow DS Big Lodge Water | TANYARD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 37.18 | 36 | 99.99%
United Utilities | HEY SHOOT LINE CSO | Hey Shoot Lane CSO | 016982504 | WAR0112 | SO | CSO on Sewer Network | SJ6760095960 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 99.99% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | HEY STREET (PLAYGROUND) CSO (32017) | Hey Street CSO | 017180621 | PEN0085 | SO | CSO on Sewer Network | SD8646038240 | GB112071065130 | Walverden Water | HENDON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 519.56 | 39 | 99.98%
United Utilities | HEYSHAM VILLAGE PUMPING STATION | Heysham Village PS | 017370153 | LAN0043 | SO | Storm Discharge at Pumping Station | SD4100061990 | GB641211171000 | Morecambe Bay | MORECAMBE BAY | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | HEYWOOD (BOTANY STW) CSO | Heywood (Botany STW) CSO | 016950082 | ROC0139 | SO | CSO on Sewer Network | SD8460011500 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 940.3 | 90 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HEYWOOD ROAD CSO 091YZ | Heywood Road CSO | 016993905 | BRY0042 | SO | CSO on Sewer Network | SD8191003931 | GB112069061451 | Irwell (Croal to Irk) | CULVERT OF PRESTWICH CLOUGH | n/a | n/a | Commissioned in 2018 - full year data expected | 0.97 | 3 | 100%
United Utilities | HIBEL ROAD CSO 27075 | Hibel Road CSO | 016982179 | MAC0146 | SO | CSO on Sewer Network | SJ9177074450 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | n/a | n/a | Commissioned in 2018 - full year data expected | 55.56 | 23 | 100%
United Utilities | HIGH BENTHAM WWTW (HGHBE) | HIGH BENTHAM WwTW | 017260004 | 17260004 | ST | Storm Tank at WwTW | SD6589069140 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Commissioned in 2019 - full year data expected | 1237.95 | 102 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HIGH BENTHAM WWTW (HGHBE) | HIGH BENTHAM WwTW | 017260004 | 17260004 | SO | Inlet CSO at WwTW | SD6589069140 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Commissioned in 2019 - full year data expected | 366.86 | 95 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HIGH BRIDGE COMBINED SEWER OVERFLOW | HIGH BRIDGE CSO | 01WIG0081 | WIG0081 | SO | CSO on Sewer Network | SJ6715099750 | GB112069060810 | Bedford Brook | BEDFORD BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HIGH HILL ROAD CSO | High Hill Road | EPRQB3596AP | PEA0020 | SO | CSO on Sewer Network | SK0078486172 | GB112069060970 | Sett | CULVERTED TRIBUTARY RIVER SETT | N/A | N/A | Commissioned in 2019 - full year data expected | 20.83 | 17 | 100%
United Utilities | HIGH LEGH STW | HIGH LEGH WwTW | 016910006 | 16910006 | SO | Inlet CSO at WwTW | SJ7065083900 | 169 | #N/A | AGDEN BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | HIGH ST WEST CSO (21120) | High Street West CSO (AKA Dinting Lane CSO) | 016892339 | PEA0030 | SO | CSO on Sewer Network | SK0225094190 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | GLOSSOP BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HIGH ST WEST CSO (21120) | High Street West CSO | 016892339 | PEA0028 | SO | CSO on Sewer Network | SK0225094190 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | GLOSSOP BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 222.53 | 32 | 76.39% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | HIGH STREET WORKINGTON CSO | High Street (Workington) Combined Sewer Overflow (Site ID 02633) (ALL0006) | 017580412 | ALL0006 | SO | CSO on Sewer Network | NY0096028430 | GB112075070520 | Derwent - conf Cocker to tidal | STAN BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 177.26 | 78 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HIGH STREET/MOORS LANE CSO | High Street/Moors Lane CSO | 01VRY0059 | VRY0059 | SO | CSO on Sewer Network | SJ5140078190 | GB112068060500 | Weaver (Dane to Frodsham) | MAIN DRAIN (TRIB RIVER WEAVER) | N/A | N/A | Commissioned in 2016 - full year data expected | 35.57 | 44 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | HIGHCROSS ROAD CSO | Highcross Road CSO | 017280298 | WYR0061 | SO | CSO on Sewer Network | SD3622038690 | GB112072066120 | Hillylaid Pool - Tidal Wyre | MAIN DYKE TRIB OF WYRE ESTUARY | N/A | N/A | Commissioned in 2016 - full year data expected | 0.23 | 1 | 100%
United Utilities | HIGHER BENTS LANE/NEWLYN DR CSO | Higher Bents Lane/Newlyn Road CSO | 01STK0008 | STK0008 | SO | CSO on Sewer Network | SJ9236091120 | GB112069061000 | Goyt (Etherow to Mersey) | BREDBURY STREAM VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 1.63 | 8 | 100%
United Utilities | HIGHER PERRY ST/BLACK LAUREL ST CSO | HIGHER PERRY STREET/BACK LAUREL CSO | 01BBN0118 | BBN0118 | SO | CSO on Sewer Network | SD6964022710 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 175.23 | 87 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HIGHFIELD AVENUE CSO | Highfield Avenue CSO | 016982697 | WAR0105 | SO | CSO on Sewer Network | SJ5712088130 | GB112069060990 | Whittle Brook (Mersey Estuary) | TRIB WHITTLE BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 25.5 | 14 | 100%
United Utilities | HILL STREET CSO | Hill Street CSO | 017190786 | HYN0027 | SO | CSO on Sewer Network | SD7654026610 | GB112071065040 | Hyndburn | WOODNOOK WATER | N/A | N/A | Commissioned in 2019 - full year data expected | 1.7 | 7 | 100%
United Utilities | HILLHOUSE WWTW | HILLHOUSE WwTW | 016930111 | 16930111 | ST | Storm Tank at WwTW | SD3501005590 | GB112069061442 | Alt DS Bull Bridge | HEY COP DRAIN, TRIB RIVER ALT | n/a | n/a | Commissioned in 2018 - full year data expected | 694.77 | 73 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HILLKIRK STREET CSO (282I9) | Hillkirk Street CSO | 016982726 | MAN0298 | SO | CSO on Sewer Network | SJ8615098500 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | HIND STREET CSO | Hind Street CSO | 016881946 | BOL0110 | SO | CSO on Sewer Network | SD7355009170 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 7 | 6 | 99.88%
United Utilities | HINDLE STREET CSO | Hindle Street CSO | 017190774 | BBN0162 | SO | CSO on Sewer Network | SD6901022680 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 9.23 | 26 | 98.73%
United Utilities | HINDLEY PUMPING STATION 50105 HINDL | Hindley PS | 016920132 | WIG0255 | SO | Storm Discharge at Pumping Station | SD6084002390 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Commissioned in 2016 - full year data expected | 386.86 | 68 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HM BORSTAL CSO | Adjacent HM Borstal Hindley CSO | 016983227 | WIG0050 | SO | CSO on Sewer Network | SD6175002350 | GB112069064520 | Hey/Borsdane Brook | BROOKSIDE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.13 | 1 | 100%
United Utilities | HOLDEN FOLD LANE CSO | Holden Fold Lane CSO | 016941057 | OLD0094 | SO | CSO on Sewer Network | SD9161007190 | GB112069061161 | Irk (Sourtce to Wince Brook) | LUZLEY BRROK | N/A | N/A | Commissioned in 2019 - full year data expected | 12.67 | 15 | 100%
United Utilities | HOLLINWOOD CEMETERY CSO | Hollinwood Cemetry CSO | 01OLD0074 | OLD0074 | SO | CSO on Sewer Network | SD9116001881 | GB112069061152 | Medlock (Lumb Brook to Irwell) | LORDS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 58.23 | 41 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOLLOW LANE/OLD HARREL LANE CSO | Hollow Lane/Harrel Lane CSO | 01BRW0036 | BRW0036 | SO | CSO on Sewer Network | SD2194069338 | GB112074069790 | Mill Beck (Poaka Beck) | MILL BECK VIA ROOSE BRIDGE | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | HOLLY STREET/NEW SPRINGS CSO | HOLLY STREET / NEW SPRINGS CSO | 01WIG0015 | WIG0015 | SO | CSO on Sewer Network | SD5984007060 | GB112070064780 | Douglas - Mid | YELLOW BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 34.67 | 25 | 100%
United Utilities | HOLME STATION CSO 391HY LAK0046 | Holme Station CSO | 017370154 | LAK0046 | SO | CSO on Sewer Network | SD5227077300 | GB112073071050 | Holme Beck | EWAN MILL BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 85.47 | 5 | 100%
United Utilities | HOLME STATION CSO 391HY LAK0046 | Holme Street/Chapel Street CSO | 017370154 | EDE0061 | SO | CSO on Sewer Network | SD5227077300 | GB112073071050 | Holme Beck | EWAN MILL BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.67 | 4 | 100%
United Utilities | HOLME WWTW | HOLME ROAD CSO | 017370138 | SRI0004 | SO | CSO on Sewer Network | SD5179078540 | GB112073071050 | Holme Beck | HOLME BECK VIA SWS | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 202.2 | 56 | 75.38% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOLME WWTW | HOLME WwTW | 017370138 | 17370138 | ST | Storm Tank at WwTW | SD5179078540 | GB112073071050 | Holme Beck | HOLME BECK VIA SWS | N/A | N/A | Commissioned in 2016 - full year data expected | 728.72 | 55 | 95.63% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | HOLMES CHAPEL STW | HOLMES CHAPEL WwTW | 016810081 | 16810081 | ST | Storm Tank at WwTW | SJ7515067590 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Commissioned in 2019 - full year data expected | 942.07 | 65 | 98.63% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOLT LANE FAILSWORTH SSO | Holt Lane (Failsworth ) SSO | 016982213 | OLD0122 | SO | CSO on Sewer Network | SD9028000680 | GB112069061152 | Medlock (Lumb Brook to Irwell) | LORDS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.27 | 2 | 99.46%
United Utilities | HOLTS LANE DETENTION TANK | Holts Lane Detention Tanks | NPSWQD001283 | WYR0084 | SO | CSO on Sewer Network | SD3552038670 | GB112072066120 | Hillylaid Pool - Tidal Wyre | MAIN DYKE | Lune (Wyre) | Fleetwood | Commissioned in 2017 - full year data expected | 8.22 | 8 | 99.97%
United Utilities | HONEY HOLME LANE CSO | Honey Holme Lane CSO | 01BUR0014 | BUR0014 | SO | CSO on Sewer Network | SD8694029140 | GB112071065060 | Calder - headwaters to conf Brun | RIVER CALDER | North Wirral East | N/A | Commissioned in 2017 - full year data expected | 509.97 | 93 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOOLEY BRIDGE CSO | Hooley Bridge CSO | 016993763 | ROC0031 | SO | CSO on Sewer Network | SD8544011600 | GB112069064600 | Roch (Spodden to Irwell) | THE RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 316.9 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOOTON ROAD CSO 181ZR | HOOTON ROAD CSO | 01ELL0009 | ELL0009 | SO | CSO on Sewer Network | SJ3549078440 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | DIBBINSDALE BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 600.07 | 66 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOREST LANE COMBINED SEWER OVERFLOW | Horest Lane CSO | 016982961 | OLD0153 | SO | CSO on Sewer Network | SD9705009250 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 0.53 | 1 | 98.64%
United Utilities | HORNBY STW | HORNBY WwTW | 017270017 | 17270017 | SO | Inlet CSO at WwTW | SD5805068390 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Commissioned in 2020 - full year data expected | 1598.85 | 94 | 99.98% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - December
United Utilities | HORTON-IN-RIBBLESDALE STW | HORTON-IN-RIBBLESDALE WwTW | 017160039 | 17160039 | ST | Storm Tank at WwTW | SD8071572125 | GB112071065640 | Ribble - Brants Ghyll to conf Stainforth Beck | RIVER RIBBLE | N/A | N/A | Commissioned in 2019 - full year data expected | 1233.69 | 111 | 100% |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Scheduled
United Utilities | HORWICH WASTEWATER TREATMENT WORKS | HORWICH WwTW | 017050012 | 17050012 | ST | Storm Tank at WwTW | SD6264010763 | GB112070064850 | Douglas - Upper | PEARL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 1246.04 | 88 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HORWICH WASTEWATER TREATMENT WORKS | HORWICH WwTW | 017050012 | 17050012 | SO | Inlet CSO at WwTW | SD6264010763 | GB112070064850 | Douglas - Upper | PEARL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 871.71 | 77 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOUGH HILL ROAD/GRASSCROFT ST CSO | HOUGH HILL ROAD / GRASSCROFT STREET CSO | 01TAM0132 | TAM0132 | SO | CSO on Sewer Network | SJ9645098180 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.1 | 3 | 100%
United Utilities | HOUGH LANE BACK CSO | Hough Lane Back CSO | 016982928 | BOL0207 | SO | CSO on Sewer Network | SD7193013120 | GB112069064570 | Eagley Brook | EAGLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | HOUGH LANE EAGLEY BRIDGE CSO 073DL | HOUGH LANE/EAGLEY BRIDGE CSO | 01BOL0150 | BOL0150 | SO | CSO on Sewer Network | SD7195013160 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 113.2 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HOYLAKE ROAD/CHAPELHILL CSO | Hoylake Road/Chapelhill Road CSO | 016881732 | WIR0124 | SO | CSO on Sewer Network | SJ2764090310 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | NORTH WIRRAL (EAST) | Moreton | Commissioned in 2016 - full year data expected | 66.2 | 18 | 100%
United Utilities | HUDDERSFIELD ROAD CSO (449BD) | Huddersfield Road CSO | 016993729 | TAM0098 | SO | CSO on Sewer Network | SJ9723098810 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | CULVERT TO RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 8.7 | 38 | 100%
United Utilities | HULTON LANE ENDS STW | HULTON LANE ENDS WwTW | 016950037 | 16950037 | SO | Inlet CSO at WwTW | SD7630004030 | GB112069061451 | Irwell (Croal to Irk) | UNITY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 441.48 | 53 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HUNCOAT PS | Nearer Holker House Farm | 01HYN0050 | HYN0050 | SO | Storm Discharge at Pumping Station | SD7695030690 | GB112071065490 | Calder - Pendle Water to conf Ribble | CLOUGH BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 10.62 | 4 | 99.99%
United Utilities | HUNSONBY CSO (171ME) | Hunsonby CSO | 017680354 | EDE0108 | SO | CSO on Sewer Network | NY5807035440 | GB102076073810 | Robberby Water | ROBBERBY WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | HUNT LANE COMBINED SEWER OVERFLOW | Hunt Lane CSO | 016950499 | OLD0105 | SO | CSO on Sewer Network | SD9057004990 | GB112069061120 | Wince Brook | STOCK BROOK CULVERT VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 6.69 | 28 | 100%
United Utilities | HUNTS BANK COMBINED SEWER OVERFLOW | HUNTS BANK CSO | 01MAN0176 | MAN0176 | SO | CSO on Sewer Network | SJ8897098920 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | HURST GREEN WWTW | Hurst Green WwTW | 017160040 | 17160040 | ST | Storm Tank at WwTW | SD6910037750 | GB112071065500 | Ribble - conf Calder to tidal | DEAN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 2694.46 | 155 | 99.89% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HURSTHEADS LANE/GREEN LANE CSO | Hurstheads Lane/Green Lane CSO | NPSWQD010893 | STK0009 | SO | CSO on Sewer Network | SJ9356090430 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | 335.01 | 81 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | HUTTON ROOF STW | HUTTON ROOF WwTW | 017370069 | 17370069 | SO | Inlet CSO at WwTW | SD5705077900 | GB112073071080 | Lupton (Farleton) Beck | SEALFORD BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HUYTON FARM PUMPING STATION | Huyton Farm PS | 016997049 | KNW0006 | SO | Storm Discharge at Pumping Station | SJ4234092560 | GB112069060580 | Alt | UN-NAMED TRIB. OF RIVER ALT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HUYTON WASTEWATER TREATMENT WORKS | HUYTON WwTW | 016930121 | 16930121 | SO | Inlet CSO at WwTW | SJ4473088840 | GB112069060680 | Netherley Brook | DITTON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 1584.82 | 104 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HUYTON WASTEWATER TREATMENT WORKS | HUYTON WwTW | 016930121 | 16930121 | ST | Storm Tank at WwTW | SJ4473088840 | GB112069060680 | Netherley Brook | DITTON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 187.69 | 35 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | HYCEMOOR WWTW BOTHH | BOOTLE / HYCEMOOR WwTW | 017470188 | 17470188 | SO | Inlet CSO at WwTW | SD0760090000 | 355 | #N/A | IRISH SEA | RAVENGLASS | N/A | Commissioned in 2018 - full year data expected | 606.9 | 55 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HYDE ROAD (DENTON) CSO | HYDE ROAD Denton CSO | 01TAM0069 | TAM0069 | SO | CSO on Sewer Network | SJ8900095910 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | 0 | N/A | N/A | Commissioned in 2020 - full year data expected | 137.37 | 66 | 91.57% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | HYDE WASTEWATER TREATMENT WORKS | HYDE WwTW | 016940088 | 16940088 | SO | Inlet CSO at WwTW | SJ9379094840 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | HYDE WASTEWATER TREATMENT WORKS | HYDE WwTW | 016940088 | 16940088 | ST | Storm Tank at WwTW | SJ9379094840 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | HYNDBURN WWTW HYNBD | Hyndburn WwTW | 017160008 | 17160008 | ST | Storm Tank at WwTW | SD7562033370 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER (RIBBLE) | n/a | n/a | Commissioned in 2018 - full year data expected | 810.76 | 79 | 99.63% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ILLINGWORTH AVENUE | Illingworth Avenue CSO | 016982691 | TAM0161 | SO | CSO on Sewer Network | SJ9727098430 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | STOCKS BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | IN FIELD POULTON M.H. 292 CSO | In Field, Poulton M/H 292 | 01WYR0020 | WYR0020 | SO | CSO on Sewer Network | SD3528037971 | GB112072066120 | Hillylaid Pool - Tidal Wyre | UNNAMED TRIBUTARY OF MAIN DYKE | LUNE (WYRE ESTUARY) | Fleetwood | Commissioned in 2016 - full year data expected | 12.07 | 19 | 100%
United Utilities | IN FIELDS REAR OF 36 EAST DRIVE CSO | In fields at rear of 36 East Drive CSO | 016982743 | SAL0153 | SO | CSO on Sewer Network | SD7886001310 | GB112069061430 | Folly Brook and Salteye Brook. | FOLLY BROOK VIA A SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 20.57 | 16 | 91.8%
United Utilities | IN FRONT OF NO.19 BEAR STREET CSO | Bear Street CSO | NPSWQD010104 | BUR0037 | SO | CSO on Sewer Network | SD8046033002 | GB112071065080 | Green Brook | SWEET CLOUGH TRIB GREEN BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 3.03 | 12 | 100%
United Utilities | INCE CEMETARY CSO | Ince Cemetery CSO | 017081358 | WIG0223 | SO | CSO on Sewer Network | SD5867004010 | GB112070061610 | Poolstock Brook | INCE BROOK | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | INFIRMARY STREET CARLISLE CSO | Infirmary Street (Carlisle) CSO | 017680309 | CAR0059 | SO | CSO on Sewer Network | NY3883056370 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | LEEDS/LIVERPOOL CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 23.88 | 20 | 99.95%
United Utilities | INFIRMARY STREET CSO 05050 | Infirmary Street CSO | 01BBN0027 | BBN0027 | SO | CSO on Sewer Network | SD6789026930 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | LEEDS/LIVERPOOL CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | INGLEBROUGH WAY BOW LANE CSO 40040 | Ingleborough Way/Bow Lane CSO | 017081363 | SRI0066 | SO | CSO on Sewer Network | SD5494022520 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 159.23 | 57 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | INGLETON STW | INGLETON WwTW | 017260005 | 17260005 | ST | Storm Tank at WwTW | SD6868072620 | GB112072071610 | Greta | RIVER GRETA | n/a | n/a | Commissioned in 2018 - full year data expected | 3700.69 | 183 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | INSKIP STREET (082AK) CSO | INSKIP STREET CSO | 01BUR0022 | BUR0022 | SO | CSO on Sewer Network | SD7939033840 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 239.93 | 85 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | IREBY WWTW | IREBY WwTW | 017570071 | 17570071 | SO | Inlet CSO at WwTW | NY2405039260 | GB112075073630 | Ellen (upper) | RIBER ELLEN | N/A | N/A | Commissioned in 2020 - full year data expected | 382.87 | 88 | 99.99% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | IRLAM WASTEWATER TREATMENT WORKS | IRLAM WwTW | 016940133 | 16940133 | ST | Storm Tank at WwTW | SJ7018092020 | GB112069061420 | Glaze | RIVER GLAZE (GLAZE BROOK) | N/A | N/A | Commissioned in 2020 - full year data expected | 2672.47 | 145 | 100% |  |  | Performance - GW inundation | Scheduled
United Utilities | IRLAM WASTEWATER TREATMENT WORKS | IRLAM WwTW | 016940133 | 16940133 | SO | Inlet CSO at WwTW | SJ7018092020 | GB112069061420 | Glaze | RIVER GLAZE (GLAZE BROOK) | N/A | N/A | Commissioned in 2020 - full year data expected | 300.25 | 72 | 99.93% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | IRTHINGTON PS | Irthington PS | 017680326 | CAR0081 | SO | Storm Discharge at Pumping Station | NY4992061620 | GB102076073981 | Irthing DS Crammel Linn Waterfall | TRIB RIVER IRTHING | N/A | N/A | Commissioned in 2019 - full year data expected | 21.5 | 7 | 100%
United Utilities | IRVINES FARM CSO | Irvine's Farm CSO | 017091502 | WIG0172 | SO | CSO on Sewer Network | SD5403006540 | GB112070064820 | Douglas - Lower | ACKHURST BROOK TRIB R DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 391.51 | 88 | 74.11% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | IRWELL VALE PS | Irwell Vale PS | 016982826 | ROS0073 | SO | Storm Discharge at Pumping Station | SD7906020460 | GB112069064650 | Ogden | RIVER OGDEN | N/A | N/A | Commissioned in 2020 - full year data expected | 15.03 | 13 | 93.15%
United Utilities | JACKSON STREET CSO | Jackson Street CSO | EPRQB3594RZ | STH0053 | SO | CSO on Sewer Network | SJ5220094960 | GB112069061210 | Hardshaw (Windle) Brook | HARDSHAW BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 37.02 | 29 | 99.46%
United Utilities | JANES BROOK ROAD PUMPING STATION | Janes Brook Road PS | 01SEF0068 | SEF0068 | SO | Storm Discharge at Pumping Station | SD3573015750 | GB112070064830 | Three Pool's Waterway | FINE JANE'S BROOK | RIBBLE | Southport | Commissioned in 2016 - full year data expected | 156.69 | 9 | 99.95%
United Utilities | JCT OF MANCHESTER RD/STATION RD CSO | Junction of Manchester/Station Road CSO | 01BOL0142 | BOL0142 | SO | CSO on Sewer Network | SD6240009950 | GB112069064540 | Middle Brook | UNNAMED TRIB OF MIDDLE BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 14.6 | 37 | 100%
United Utilities | JERICHO LANE CSO | Jericho Lane CSO | 016930981 | LIV0045 | SO | CSO on Sewer Network | SJ3740085810 | 167 | #N/A | MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | JOHN LEE FOLD CSO | John Lee Fold CSO | 016982900 | ROC0012 | SO | CSO on Sewer Network | SD8737006200 | GB112069061161 | Irk (Sourtce to Wince Brook) | WHIT BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 17.73 | 6 | 100%
United Utilities | JOHN PIER SEWAGE PUMPING STATION | John Pier Sewage Pumping Station CSO | 017580294 | ALL0133 | SO | Storm Discharge at Pumping Station | NX9966029440 | 188 | #N/A | RIVER DERWENT ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 80.17 | 21 | 100%
United Utilities | JOHN STREET CSO 35020 | John Street CSO | 016993768 | ROC0034 | SO | CSO on Sewer Network | SD8583011010 | GB112069064600 | Roch (Spodden to Irwell) | MILLERS BROOK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 34.7 | 37 | 99.99%
United Utilities | JULIA SREETT CSO | Julia Street CSO | EPRQB3590DE | MAN0005 | SO | CSO on Sewer Network | SJ8357099240 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 2010.03 | 134 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | JUNC ALDER LANE/NORTH AVE CSO | Junction Alder Lane/North Avenue CSO | 016993626 | WAR0074 | SO | CSO on Sewer Network | SJ6085090020 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 6.43 | 5 | 100%
United Utilities | JUNC HUNGERFORD ROAD AND LAURESTON | Junction of Hungerford Road and Laureston Avenue CSO | 01CRE0017 | CRE0017 | SO | CSO on Sewer Network | SJ7200055500 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | DRAIN, TRIB OF VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 12.4 | 15 | 94.25%
United Utilities | JUNC PROMENADE SILVERDALE RD CSO | Arnside Promenade/Silverdale Road CSO | EPRYP3621XD | LAK0101 | SO | CSO on Sewer Network | SD4558678760 | 183 | #N/A | MORECAMBE BAY ESTUARINE WTRS | N/A | N/A | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | JUNC STRINGER ST/NEW BRIDGE LN CSO | Junction Stringer Street/New Bridge Lane CSO | 016892181 | STK0145 | SO | CSO on Sewer Network | SJ9039090700 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.33 | 2 | 100%
United Utilities | JUNC STRINGER ST/NEW BRIDGE LN CSO | Stringer Street/Newbridge Lane CSO | 01STK0089 | STK0089 | SO | CSO on Sewer Network | SJ9039090700 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | 0.03 | 1 | 100%
United Utilities | JUNCTION OF ASHTON NEW ROAD CSO | Junction of Ashton New Road CSO | 016982734 | MAN0323 | SO | CSO on Sewer Network | SJ8732097120 | GB112069061210 | Hardshaw (Windle) Brook | WINDLE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | JUNCTION OF GRAVER LN ELSMA RD CSO | Junction of GRAVER LANE and ELSMA ROAD CSO | 01MAN0104 | MAN0104 | SO | CSO on Sewer Network | SJ8896099500 | GB112069061152 | Medlock (Lumb Brook to Irwell) | BERRY BROW CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 0.4 | 2 | 100%
United Utilities | JUNCTION OF WORDSOWRTH STREET CSO | Junction of Wordsworth Street CSO | 01EDE0029 | EDE0029 | SO | CSO on Sewer Network | NY5142030380 | GB102076071020 | Eamont (Upper) | THACKA BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | K SHOES CSO 042B6 | K. Shoes, CSO | 01BRW0056 | BRW0056 | SO | CSO on Sewer Network | SD2144077990 | 344 | #N/A | BLEA BECK | Duddon and Walney | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 0.17 | 2 | 99.75%
United Utilities | KABER WASTEWATER TREATMENT WORKS | KABER WwTW | 017670011 | 17670011 | SO | Inlet CSO at WwTW | NY7953111665 | GB102076070620 | Belah (lower) | POPPING BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 405.79 | 55 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | KAY STREET CSO | Kay Street | 017180465 | BBN0137 | SO | CSO on Sewer Network | SD6957022310 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 2.3 | 16 | 100%
United Utilities | KEARSLEY PS | Kearsley PS | 016990060 | BOL0036 | SO | Storm Discharge at Pumping Station | SD7568005670 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 447.17 | 144 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KEEKLE PUMPING STATION | Keekle PS | 017470076 | COP0058 | SO | Storm Discharge at Pumping Station | NY0050016170 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | n/a | Seascale | Commissioned in 2017 - full year data expected | 966.51 | 114 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | KEEPER'S LANE CSO (472BH) | KEEPERS LANE CSO | 01VRY0081 | VRY0081 | SO | CSO on Sewer Network | SJ6253073360 | GB112068060500 | Weaver (Dane to Frodsham) | TRIB OF RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 13.27 | 12 | 97.86%
United Utilities | KENDAL WASTE WATER TREATMENT WORKS | KENDAL WwTW | 017370100 | 17370100 | ST | Storm Tank at WwTW | SD5170090790 | GB112073071460 | Kent - conf Sprint to tidal | THE RIVER KENT | Morecambe Bay Leven | n/a | September 2021 | 613.57 | 55 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation
United Utilities | KENDAL WASTE WATER TREATMENT WORKS | KENDAL WwTW | 017370100 | 17370100 | SO | Inlet CSO at WwTW | SD5170090790 | GB112073071460 | Kent - conf Sprint to tidal | THE RIVER KENT | Morecambe Bay Leven | n/a | September 2021 | 203.73 | 32 | 100%
United Utilities | KENDALL ROAD BLACKLEY CSO | Kendall Road (Blackley) Combined Sewer Overflow | 016982987 | MAN0398 | SO | CSO on Sewer Network | SD8383003360 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK VIA BIRCH BROOK CLVR | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 84.23% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | KENLIS STW | Kenlis PS | 017260145 | WYR0047 | SO | Storm Discharge at Pumping Station | SD5079043860 | GB112072066220 | Calder (Wyre) | LITTLE CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 447.75 | 70 | 98.57% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KENWORTHY LANE PS | Kenworthy Lane PS | 016982983 | MAN0385 | SO | Storm Discharge at Pumping Station | SJ8254091080 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | KENYON LANE CSO | Kenyon Lane CSO | 016982953 | MAN0352 | SO | CSO on Sewer Network | SD8770001160 | GB112069061131 | Irk (Wince to Irwell) | TRIB RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 24.18 | 21 | 99.86%
United Utilities | KEPPLE LANE(OVERFLOW C GARSTANG)CSO | Kepple Lane (Overflow 'C' Garstang) CSO | 017260029 | WYR0030 | SO | CSO on Sewer Network | SD4883044700 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | N/A | Commissioned in 2020 - full year data expected | 266.52 | 58 | 99.89% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KERN MILL LANE CSO 122BI | Kem Mill Lane CSO | 017060027 | CHR0060 | SO | CSO on Sewer Network | SD5769021680 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 88.63 | 40 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KESWICK STW | KESWICK WwTW | 017570044 | 17570044 | ST | Storm Tank at WwTW | NY2487224952 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 801.97 | 70 | 98.77% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | KIDSGROVE WWTW | KIDSGROVE WwTW | 016810083 | 16810083 | ST | Storm Tank at WwTW | SJ8284055210 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM WHEELOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 25.47 | 6 | 99.98%
United Utilities | KILN BROW COMBINED SEWER OVERFLOW | Kiln Brow CSO | 017480401 | COP0019 | SO | CSO on Sewer Network | NY0165013400 | GB112074070010 | Ehen (upper including Liza) | RIVER EHEN | N/A | St Bees | Commissioned in 2016 - full year data expected | 1.2 | 19 | 100%
United Utilities | KILN BROW PUMPING STATION | Kiln Brow WwPS | 01COP0011 | COP0011 | SO | Storm Discharge at Pumping Station | NY0165013401 | GB112074070010 | Ehen (upper including Liza) | RIVER EHEN | N/A | N/A | Commissioned in 2020 - full year data expected | 1086.53 | 49 | 87.91% | Sensor failure / issue | Resolved - October | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation
United Utilities | KING GEORGE PRESCOT CSO | King George V Memorial Playing Field | 016930642 | KNW0024 | SO | CSO on Sewer Network | SJ4613092260 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | PRESCOT BROOK TRIB DITTON BRK | N/A | N/A | Commissioned in 2019 - full year data expected | 232.4 | 54 | 96.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KING STREET CSO 072BV | KING STREET CSO | 01BOL0123 | BOL0123 | SO | CSO on Sewer Network | SD7138009370 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Commissioned in 2018 - full year data expected | 0.2 | 3 | 100%
United Utilities | KING STREET PUMPING STATION | King Street PS | 017470009 | COP0049 | SO | Storm Discharge at Pumping Station | SD1783180401 | 187 | #N/A | DUDDON ESTUARY | Duddon and Walney | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 13.93 | 26 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | KINGFISHER DRIVE CSO 092BS | Kingfisher Drive CSO | 01BRY0011 | BRY0011 | SO | CSO on Sewer Network | SD8168011790 | GB112069064600 | Roch (Spodden to Irwell) | CLVRTD SECTION GYPSY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0.63 | 3 | 100%
United Utilities | KINGFISHER WAY CSO | Kingfisher Way CSO | 016892442 | WIR0080 | SO | CSO on Sewer Network | SJ2554088920 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | NORTH WIRRAL (WEST) | Meols | Commissioned in 2016 - full year data expected | 0.17 | 2 | 52.31% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | KINGSBRIDGE ROAD CSO (289BQ) | Kingsbridge Road CSO | 01MAN0071 | MAN0071 | SO | CSO on Sewer Network | SD8546001280 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2020 - full year data expected | 135.47 | 68 | 97.38% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KINGSLEY STW | KINGSLEY WwTW | 016810084 | 16810084 | ST | Storm Tank at WwTW | SJ5677074520 | GB112068060550 | Crowton Brook | TRIB CROWTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 937.66 | 60 | 99.91% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KINGSWAY COMBINED SEWER OVERFLOW | Kingsway CSO | 016920069 | WAR0017 | SO | CSO on Sewer Network | SJ6245088010 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | Commissioned in 2016 - full year data expected | 89.82 | 136 | 97.02% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | KIRIBATI WAY CSO | Kiribati Way CSO | 016983320 | WIG0238 | SO | CSO on Sewer Network | SD6503000870 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.17 | 1 | 100%
United Utilities | KIRK BAMPTON WWTW (KIRKB) | KIRK BAMPTON WwTW | 017670126 | 17670126 | SO | Inlet CSO at WwTW | NY3025057020 | 89 | #N/A | BURGHMOOR BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 2499.44 | 297 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | KIRK BAMPTON WWTW (KIRKB) | KIRK BAMPTON WwTW | 017670126 | 17670126 | ST | Storm Tank at WwTW | NY3025057020 | 89 | #N/A | BURGHMOOR BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | KIRKBRIDE PS KIRKV ALL0107 | Kirkbride Pumping Station (Site ID KIRKV) (ALL0107) | 017580258 | ALL0107 | SO | Storm Discharge at Pumping Station | NY2293056810 | 90 | #N/A | MONKS DYKE | Solway | N/A | Commissioned in 2016 - full year data expected | 373.55 | 36 | 99.98%
United Utilities | KIRKBRIDE WWTW | Kirkbride Wastewater Treatment Works (Site ID KRKBR) (017570195) | 017580195 | 17570195 | ST | Storm Tank at WwTW | NY2365056890 | 90 | #N/A | RIVER WAMPOOL | N/A | N/A | Commissioned in 2016 - full year data expected | 275.02 | 32 | 99.9% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | KIRKBY LONSDALE STW | KIRKBY LONSDALE WwTW | 017270006 | 17270006 | ST | Storm Tank at WwTW | SD6152077880 | GB112072071690 | Lune - conf Rawthey to conf Greta | RIVER LUNE | N/A | N/A | Commissioned in 2020 - full year data expected | 481.98 | 71 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KIRKBY LONSDALE STW | KIRKBY LONSDALE WwTW | 017270006 | 17270006 | SO | Inlet CSO at WwTW | SD6152077880 | GB112072071690 | Lune - conf Rawthey to conf Greta | RIVER LUNE | N/A | N/A | Commissioned in 2020 - full year data expected | 77.37 | 45 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KIRKBY STEPHEN WWTW | Kirkby Stephen WwTW | 017670013 | 17670013 | ST | Storm Tank at WwTW | NY7717010460 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 2431.59 | 134 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting)
United Utilities | KIRKBY STEPHEN WWTW | Kirkby Stephen WwTW | 017670013 | 17670013 | SO | Inlet CSO at WwTW | NY7717010460 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | KIRKBY THORE PS | Kirkby Thore PS | 017680336 | EDE0087 | SO | Storm Discharge at Pumping Station | NY6364025290 | GB102076070930 | Trout Beck | TROUT BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 117.59 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KIRKHALL LANE CSO | Kirkhall Lane CSO | 01WIG0107 | WIG0107 | SO | CSO on Sewer Network | SD6495001370 | GB112069060820 | Westleigh Brook | 0 | N/A | N/A | Commissioned in 2019 - full year data expected | 458.6 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | KIRKHALL LANE/VICTORIA STREET CSO | Kirkhall Lane/Victoria Street CSO | EPRQB3595RE | WIG0141 | SO | CSO on Sewer Network | SD6501001510 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 73.83 | 56 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | KIRKHAM COMBINED SEWER OVERFLOW | Kirkham CSO | 017180578 | FYL0044 | SO | CSO on Sewer Network | SD4248032450 | GB112071065670 | Dow Brook | CARR BROOK, TRIB. OF DOW BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 111.67 | 26 | 100%
United Utilities | KIRKHOUSE HALLBANKGT PS 10531 | Kirkhouse (Hallbankgate) PS | 017680373 | CAR0094 | SO | Storm Discharge at Pumping Station | NY5651060080 | GB102076074050 | Quarry Beck | MILTON BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 22.57 | 20 | 99.97% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | KIRKLAND STW | KIRKLAND WwTW | 017470029 | 17470029 | SO | Inlet CSO at WwTW | NY0733017430 | GB112074070010 | Ehen (upper including Liza) | HAWES GILL | N/A | N/A | Commissioned in 2020 - full year data expected | 92.03 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KIRKOSWALD STW | KIRKOSWALD WwTW | 017670065 | 17670065 | ST | Storm Tank at WwTW | NY5471041200 | GB102076073940 | Eden - Eamont to tidal | TRIB RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 23.01 | 13 | 99.9%
United Utilities | KIRKOSWALD VILLAGE PUMPING STATION | Kirkoswald PS | 01EDE0067 | EDE0067 | SO | Storm Discharge at Pumping Station | NY5553041150 | GB102076073840 | Raven Beck | RAVEN BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 9.72 | 6 | 100%
United Utilities | KIRKWAY COMBINED SEWER OVERFLOW | Kirkway CSO | 016950343 | ROC0136 | SO | CSO on Sewer Network | SD8724005591 | GB112069061120 | Wince Brook | WINCE BROOK, TRIB OF RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 163.72 | 62 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KNOTT END PUMPING STATION | Seeds Pumping Station (Site ID 52541) (WYR0035) | 017260103 | WYR0035 | SO | CSO on Sewer Network | SD3458048370 | GB641211171000 | Morecambe Bay | RIVER WYRE ESTUARY | Lune (Broadfleet and Plover Scar) | Fleetwood | Commissioned in 2017 - full year data expected | 12.47 | 3 | 100%
United Utilities | KNOWLE STREET CSO 442BX | Knowle Street CSO | 016993732 | TAM0097 | SO | CSO on Sewer Network | SJ9666098600 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | THE RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 0.27 | 2 | 97.29%
United Utilities | KNUTSFORD MAIN PUMPING STATION | Knutsford Main PS | 01MAC0144 | MAC0144 | SO | Storm Discharge at Pumping Station | SJ7548078730 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | MOOR POOL | n/a | n/a | Commissioned in 2017 - full year data expected | 45.71 | 14 | 100%
United Utilities | KNUTSFORD RD/GRAMMAR SCHOOL RD CSO | KNUTSFORD / GRAMMAR SCHOOL ROAD CSO | 01WAR0073 | WAR0073 | SO | CSO on Sewer Network | SJ6269086950 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 446.77 | 66 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | KNUTSFORD WWTW | KNUTSFORD WwTW | 016910007 | 16910007 | ST | Storm Tank at WwTW | SJ7680079910 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | BIRKIN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | LABURNUM GROVE | Laburnham Grove | 01HAL0127 | HAL0127 | SO | CSO on Sewer Network | SJ5176082090 | 169 | #N/A | #N/A | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | LADY BECK CSO (172CN) | Lady Beck CSO | 01EDE0005 | EDE0005 | SO | CSO on Sewer Network | NY5012026861 | GB102076071020 | Eamont (Upper) | LADY BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | LADYBRIDGE LANE CSO | Ladybridge Lane (Near Ladybridge Brow) CSO | 01BOL0118 | BOL0118 | SO | CSO on Sewer Network | SD6864008920 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 204.97 | 60 | 86.14% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LADYBRIDGE LANE CSO | Ladybridge Lane CSO | 016982193 | BOL0173 | SO | CSO on Sewer Network | SD6843008910 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 131.53 | 28 | 99.97%
United Utilities | LAMALEACH CSO 19008 | Lamaleach CSO | 01FYL0002 | FYL0002 | SO | CSO on Sewer Network | SD4250028200 | 176 | #N/A | POOL STREAM | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 275.89 | 35 | 100%
United Utilities | LANCASTER RD RADCLIFFE RD CSO 372CC | Lancaster/Radcliffe Road | 01SAL0075 | SAL0075 | SO | CSO on Sewer Network | SJ7840099700 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 39.33% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | LANCASTER ROAD/HAYFIELD ROAD TANK | Lancaster Road/Hayfield Road Detention Tank | 016993482 | SAL0192 | SO | CSO on Sewer Network | SJ7877099770 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK(MANC SHIP) VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 4.58 | 38 | 99.88%
United Utilities | LANCASTER STREET CSO 432CD | Lancaster Street CSO | 016982666 | STK0101 | SO | CSO on Sewer Network | SJ9029090670 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | LANCASTER WWTW LANCA | Lancaster WwTW | 017270050 | 17270050 | ST | Storm Tank at WwTW | SD4570058710 | GB531207212100 | LUNE | LUNE ESTUARY | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 846.71 | 49 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LANDGATE SPS | Landgate PS | 017020034 | WIG0154 | SO | Storm Discharge at Pumping Station | SD5715001450 | GB112070061610 | Poolstock Brook | PARK BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LANESHAWBRIDGE SCHOOL LANE CSO | Laneshawbridge School Lane Combined Sewer Overflow | 01PEN0029 | PEN0029 | SO | CSO on Sewer Network | SD9230040670 | GB112071065210 | Colne Water (Laneshaw) | COLNE WATER | N/A | N/A | Commissioned in 2019 - full year data expected | 0.4 | 4 | 100%
United Utilities | LANGDALE ROAD CSO 432KA | Langdale Road CSO | 01STK0015 | STK0015 | SO | CSO on Sewer Network | SJ8905084710 | GB112069060940 | Micker Brook | CARR BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 11.07 | 24 | 93.45%
United Utilities | LANGLEY RD NORTH CSO | Langley Road North CSO | 016982973 | SAL0187 | SO | CSO on Sewer Network | SD8081001070 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LANGLEY ROAD CSO | Langley Road CSO | 016993610 | SAL0092 | SO | CSO on Sewer Network | SD8070001000 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Commissioned in 2020 - full year data expected | 105.13 | 73 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LANGRIGG PS | Langrigg PS | 017580268 | ALL0117 | SO | Storm Discharge at Pumping Station | NY1728046450 | GB102075073490 | Holme Dub | LANGRIGG BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 112.64 | 18 | 98.58%
United Utilities | LANGWATHBY COMBINED SEWER OVERFLOW | Langwathby CSO | EPRRP3420XG | EDE0120 | SO | Storm Discharge at Pumping Station | NY5652534220 | GB102076073800 | Briggle Beck | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 322.33 | 82 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LANGWATHBY WWTW | LANGWATHBY WwTW | 017670066 | 17670066 | ST | Storm Tank at WwTW | NY5590034100 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 1430.03 | 80 | 99.9% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | LANGWOOD BROOK CSO | Langwood Brook CSO | 016993533 | ROS0037 | SO | CSO on Sewer Network | SD7900022740 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | CLVRT'D SECTION LANGWOOD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 4.29 | 11 | 100%
United Utilities | LARBURNUM PARK PUMPING STATION | Hope Terrace PS | NPSWQD011002 | LAN0061 | SO | Storm Discharge at Pumping Station | SD4915069680 | 185 | #N/A | BLACK DIKE, TRIB KEER ESTUARY | Morecambe Bay East | Morecambe North | Commissioned in 2017 - full year data expected | 97.01 | 36 | 100%
United Utilities | LARK HILL/BROOKHOUSE LANE CSO | Lark Hill/Brook House Lane CSO | 017180473 | BBN0148 | SO | CSO on Sewer Network | SD6874028700 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 1.2 | 8 | 100%
United Utilities | LATHBURY ROAD ADJ TO FOOTPATH CSO | Lathbury Road (Adjacent to the footpath) Combined Sewer Overflow | 01MAN0087 | MAN0087 | SO | CSO on Sewer Network | SD8604000860 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.2 | 2 | 100%
United Utilities | LATHBURY ROAD/SILCHESTER DRIVE CSO | LATHBURY ROAD / SILCHESTER DRIVE CSO | 01MAN0136 | MAN0136 | SO | CSO on Sewer Network | SD8583500640 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 7.43 | 13 | 100%
United Utilities | LATTINGS CLOSE CSO 028NF | Lattrigg Close | 017580252 | ALL0095 | SO | CSO on Sewer Network | NY2758023890 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER GRETA | n/a | n/a | Commissioned in 2017 - full year data expected | 1 | 8 | 100%
United Utilities | LATTRIGG RD CSO 022CJ | Lattrigg Road CSO | 017480431 | COP0044 | SO | CSO on Sewer Network | NX9803015660 | 356 | #N/A | CLVRT POW BECK VIA SWS | n/a | n/a | Commissioned in 2017 - full year data expected | 21.73 | 12 | 100%
United Utilities | LAUNDRY ST/DUCHY RD CSO | Laundry Street/Duchy Road Combined Sewer Overflow | 016993761 | SAL0082 | SO | CSO on Sewer Network | SD8153000410 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 333.63 | 61 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LAWTON GATE WWTW | LAWTON GATE WwTW | 016810085 | 16810085 | ST | Storm Tank at WwTW | SJ8090056490 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM | N/A | N/A | Commissioned in 2019 - full year data expected | 435.6 | 39 | 100%
United Utilities | LAWTON GATE WWTW | LAWTON GATE WwTW | 016810085 | 16810085 | SO | Inlet CSO at WwTW | SJ8090056490 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM | N/A | N/A | Commissioned in 2019 - full year data expected | 52.13 | 17 | 100%
United Utilities | LAWTON ROAD WESLEY AVE CSO 132CM | Lawton Road/Wesley Avenue CSO | 016892429 | CON0028 | SO | CSO on Sewer Network | SJ7989056282 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BROOK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 1.93 | 4 | 100%
United Utilities | LAZONBY PS AND CSO | Lazonby PS and CSO | 017670241 | EDE0073 | SO | Storm Discharge at Pumping Station | NY5516039980 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 93.55 | 61 | 99.87% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LEA GATE PUMPING STATION | Lea Gate PS | 017180631 | PRE0113 | SO | Storm Discharge at Pumping Station | SD4789030020 | 176 | #N/A | SAVICK BK, TRIB OF RIBBLE EST | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 136.43 | 35 | 99.98%
United Utilities | LEACH LANE ST HELENS CSO | Leach Lane (St. Helens) CSO | 016982980 | STH0112 | SO | CSO on Sewer Network | SJ5265092360 | GB112069061170 | Sutton Brook | SUTTON MILL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 17.3 | 20 | 100%
United Utilities | LEADALE ROAD CSO 402CQ | Leadale Road CSO | 01SRI0018 | SRI0018 | SO | CSO on Sewer Network | SD5285022270 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 18.6 | 16 | 100%
United Utilities | LEASOWE ROAD CSO | Leasowe Road CSO | 016892469 | WIR0060 | SO | CSO on Sewer Network | SJ2905092110 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 354.62 | 51 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery
United Utilities | LEE ROAD CSO (369BA) | Lee Road CSO | 016982935 | ROS0077 | SO | CSO on Sewer Network | SD8625021810 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2020 - full year data expected | 0.03 | 1 | 100%
United Utilities | LEIGH SSO | Green Lane Leigh | 016920277 | WIG0211 | SO | CSO on Sewer Network | SD6743000380 | GB112069060810 | Bedford Brook | PEN LEACH BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LEIGH STW | LEIGH WwTW | 016920134 | 16920134 | SO | Inlet CSO at WwTW | SJ6581099000 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1131.53 | 92 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LEIGH STW | LEIGH WwTW | 016920134 | 16920134 | ST | Storm Tank at WwTW | SJ6581099000 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1131.53 | 92 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LENNOX GATE PUMPING STATION | Lennox Gate PS | 017180567 | BPL0022 | SO | Storm Discharge at Pumping Station | SD3177533085 | GB112071065651 | Main Drain (Ribble) | IRISH SEA | N/A | Blackpool (South) | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | LEVANT MILL FOOTBRIDGE CSO (O82CV) | Levant Mill Footbridge CSO | 01BUR0027 | BUR0027 | SO | CSO on Sewer Network | SD7958033440 | GB112071065080 | Green Brook | GREEN BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.07 | 1 | 100%
United Utilities | LEVER STREET NO 3 CSO | Lever Street Number 3 CSO | 016983263 | BOL0236 | SO | CSO on Sewer Network | SD7196007830 | GB112069064540 | Middle Brook | JENNY BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 46.9 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LEVER STREET NO 5 CSO 078CD | Lever Street Number 5 CSO | 016983265 | BOL0238 | SO | CSO on Sewer Network | SD7196007833 | GB112069064540 | Middle Brook | JENNY BECK A TRIB OF RVR CROAL | n/a | n/a | Commissioned in 2018 - full year data expected | 2.03 | 6 | 100%
United Utilities | LEVER STREET NO1 CSO | Lever Street Number 1 CSO | 016983261 | BOL0234 | SO | CSO on Sewer Network | SD7196007831 | GB112069064540 | Middle Brook | A CULVERTED SECTION JENNY BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 2.33 | 12 | 100%
United Utilities | LEYLAND LANE (SEVEN STARS) CSO | Leyland Lane (Seven Stars) CSO | 017081265 | SRI0057 | SO | CSO on Sewer Network | SD5276021700 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 41.6 | 29 | 100%
United Utilities | LEYLAND WASTE WATER TREATMENT WORKS | LEYLAND WwTW | 017060018 | 17060018 | ST | Storm Tank at WwTW | SD5215020870 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | LIGHTBOUNDS RD LVAINE AVE CSO 072CO | LIGHTBOUNDS ROAD / LOUVAINE AVENUE CSO | 01BOL0070 | BOL0070 | SO | CSO on Sewer Network | SD6888011330 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 0.5 | 4 | 100%
United Utilities | LIGHTFOOT LANE PS | Lightfoot Lane PS | 01PRE0081 | PRE0081 | SO | Storm Discharge at Pumping Station | SD5115033320 | GB112072065760 | Woodplumpton Brook | UNAMED TRIB WOODPLUMPTON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LIMBRICK PUMPING STATION | Limbrick Pumping Station (12024) (CHR0030) | 01CHR0030 | CHR0030 | SO | Storm Discharge at Pumping Station | SD6003016340 | GB112070064951 | Yarrow US Big Lodge Water | RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 0.1 | 3 | 100%
United Utilities | LIME STREET SPS | Lime Street Wastewater Network Pumping Station | 017670160 | CAR0005 | SO | Storm Discharge at Pumping Station | NY3999055350 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Commissioned in 2019 - full year data expected | 71.72 | 28 | 99.59%
United Utilities | LIME TREE CLOSE CSO | Lime Tree Close CSO | 016940381 | TRA0071 | SO | CSO on Sewer Network | SJ7714093810 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2020 - full year data expected | 57.73 | 18 | 99.99%
United Utilities | LIMESIDE RD/CHURCH CSO | Limeside Road CSO | 016982632 | OLD0132 | SO | CSO on Sewer Network | SD9116001880 | GB112069061152 | Medlock (Lumb Brook to Irwell) | LORDS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 91.5%
United Utilities | LIMESIDE ROAD/FOX MILL CSO | Limeside Road/Fox Mill CSO | 01OLD0075 | OLD0075 | SO | CSO on Sewer Network | SD9116001882 | GB112069061152 | Medlock (Lumb Brook to Irwell) | MOSTON BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0.77 | 3 | 100%
United Utilities | LINDAL PUMPING STATION 04509 | Lindal PS | 017370050 | BRW0072 | SO | Storm Discharge at Pumping Station | SD2471075510 | GB112073071150 | Deep Meadows Beck | TRIB OF CLARKES BECK | WALNEY EAST | N/A | Commissioned in 2016 - full year data expected | 395.54 | 95 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | LINDALE WASTEWATER TREATMENT WORKS | LINDALE WwTW | 017370073 | 17370073 | ST | Storm Tank at WwTW | SD4234280672 | GB112073071440 | Winster | RIVER WINSTER | MORECAMBE BAY EAST | N/A | Commissioned in 2018 - full year data expected | 947.62 | 68 | 99.17% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LINDRED ROAD CSO | Lindred Road CSO | 01PEN0056 | PEN0056 | SO | CSO on Sewer Network | SD8433037340 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 1498.07 | 132 | 87.96% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LINETHWAITE PUMPING STATION | Linethwaite PS | 017480475 | COP0012 | SO | Storm Discharge at Pumping Station | NX9917014000 | GB112074069990 | Pow Beck (South West Lakes) | NEEDLESS BECK | N/A | St Bees | Commissioned in 2016 - full year data expected | 9.66 | 8 | 99.93%
United Utilities | LINK ROAD COMBINED SEWER OVERFLOW | LINK ROAD CSO | 01KNW0009 | KNW0009 | SO | CSO on Sewer Network | SJ4580090090 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | LOGWOOD MILL BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 3.33 | 8 | 100%
United Utilities | LINKSVIEW ESTATE CSO 091BC | Linksview Estate CSO | 01BRY0064 | BRY0064 | SO | CSO on Sewer Network | SD8101007570 | GB112069064600 | Roch (Spodden to Irwell) | PARR BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0.2 | 2 | 100%
United Utilities | LITTLE CLIFTON STW | LITTLE CLIFTON WwTW | 017570045 | 17570045 | ST | Storm Tank at WwTW | NY0567029230 | GB112075070540 | Marron | RIVER MARRON | N/A | N/A | Commissioned in 2020 - full year data expected | 850.23 | 75 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LITTLE CORBY PS | Little Corby PS | 017680327 | CAR0082 | SO | Storm Discharge at Pumping Station | NY4765057340 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0.5 | 2 | 99.99%
United Utilities | LITTLE HULTON CSO | LITTLE HULTON CSO | 01SAL0130 | SAL0130 | SO | CSO on Sewer Network | SD7135003630 | GB112069061100 | Astley Brook (Mersey) | ASTLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LITTLE SALKELD WWTW | LITTLE SALKELD WwTW | 017680290 | 17680290 | SO | Inlet CSO at WwTW | NY5617036670 | GB102076073940 | Eden - Eamont to tidal | TRIB RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 2054.59 | 163 | 99.9% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | LITTLETON ROAD CSO | Littleton Road CSO | EPRSB3396WD | SAL0112 | SO | CSO on Sewer Network | SD8175000500 | GB112069061451 | Irwell (Croal to Irk) | THE RIVER IRWELL | N/A | N/A | Commissioned in 2020 - full year data expected | 14.27 | 12 | 63.6% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | LIVERPOOL RD CSO | Liverpool Road CSO | 016881976 | NEW0010 | SO | CSO on Sewer Network | SJ8315054910 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM | N/A | N/A | Commissioned in 2020 - full year data expected | 1023.24 | 82 | 99.89% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LIVERPOOL ROAD (HINDLEY) CSO | Liverpool Road (Hindley) CSO | 016983327 | WIG0228 | SO | CSO on Sewer Network | SD6154003260 | GB112069064520 | Hey/Borsdane Brook | TRIBUTARY OF HEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | LIVERPOOL ROAD CSO (088NF) | Liverpool Road (Burnley) CSO | 01BUR0012 | BUR0012 | SO | CSO on Sewer Network | SD8219032540 | GB112071065080 | Green Brook | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | LIVERPOOL ROAD/NEWHALL AVENUE CSO | Liverpool Road/Newhall Avenue CSO | 01SAL0054 | SAL0054 | SO | CSO on Sewer Network | SJ7530097480 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 65.03 | 68 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LIVERPOOL WWTW | LIVERPOOL WwTW | 016993397 | 16993397 | SO | Inlet CSO at WwTW | SJ3321092640 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 351.15 | 97 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LIVERPOOL WWTW | LIVERPOOL WwTW | 016993397 | 16993397 | ST | Storm Tank at WwTW | SJ3321092640 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 307.15 | 14 | 100%
United Utilities | LOCK LANE PARTINGTON CSO | Lock Lane CSO | 01TRA0035 | TRA0035 | SO | CSO on Sewer Network | SJ7088091511 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 1745.27 | 190 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LODGE BANK PUMPING STN | Lodge Bank PS | 016981230 | CHR0052 | SO | Storm Discharge at Pumping Station | SD6204020410 | GB112070064951 | Yarrow US Big Lodge Water | BRINSCALL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 126.16 | 19 | 100%
United Utilities | LODGE LANE COMBINED SEWER OVERFLOW | Lodge Lane (Near Ellams Brook) CSO | 016920211 | STH0072 | SO | CSO on Sewer Network | SJ5817096900 | GB112069061220 | Millingford (Newton) Brook | TRIB DEAN DAM | N/A | N/A | Commissioned in 2019 - full year data expected | 514.27 | 49 | 98.1% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LODGE LANE COMBINED SEWER OVERFLOW | Lodge Lane, Bewsey CSO | 016993698 | WAR0035 | SO | CSO on Sewer Network | SJ5817096900 | GB112069061220 | Millingford (Newton) Brook | ELLAMS BROOK,TRIB NEWTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 244.33 | 40 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LODGE RD, ORRELL(M.H. A4) | Lodge Road (Orrell) CSO | 01WIG0171 | WIG0171 | SO | CSO on Sewer Network | SD5328000380 | GB112069061230 | Black Brook (Mersey Estuary) | 0 | n/a | n/a | Commissioned in 2018 - full year data expected | 341.06 | 90 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LOMAX STREET CSO | Lomax Street combined sewer overflow (099AA) (BRY0033) | 016993829 | BRY0033 | SO | CSO on Sewer Network | SD7845006660 | GB112069060840 | Irwell (Roch to Croal) | THE RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 598.07 | 113 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LOMBARD GR/LORNE RD | Lombard Grove/Lorne Road CSO | 016982821 | MAN0344 | SO | CSO on Sewer Network | SJ8523093520 | GB112069061410 | Fallowfield Brook | CRINGLE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LOMESHAYE WAY CSO | Lomeshaye Way CSO | 017180488 | PEN0055 | SO | CSO on Sewer Network | SD8513037900 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 100.73 | 36 | 99.85%
United Utilities | LONDON ROAD | London Road (Nantwich) Combined Sewer Overflow (Site ID 162C7) (CRE0081) | 017160314 | CRE0081 | SO | CSO on Sewer Network | SD5528028742 | 176 | #N/A | STORM CULVERT INTO R RIBBLE | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 75.6% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | LONDON ROAD | London Road CSO | 017160314 | PRE0005 | SO | CSO on Sewer Network | SD5528028742 | 176 | #N/A | STORM CULVERT INTO R RIBBLE | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | LONG HEY ROAD CSO | Long Hey Road CSO | CM0077001 | WIR0094 | SO | CSO on Sewer Network | SJ2302083940 | GB641211630001 | Mersey Mouth | RIVER DEE (NORTH WALES) | DEE (EAST) | West Kirby | Commissioned in 2016 - full year data expected | 43.93 | 13 | 100%
United Utilities | LONG MILLGATE CSO | Long Millgate_Near Manchester Cathedral Gardens_CSO | 016993741 | MAN0160 | SO | CSO on Sewer Network | SJ8400098910 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.03 | 1 | 100%
United Utilities | LONG PRESTON WWTW LNGPR | Long Preston Wastewater Treatment Works (LNGPR) (017160041) | 017160041 | 17160041 | SO | Inlet CSO at WwTW | SD8306057620 | GB112071065600 | Long Preston Beck | LONG PRESTON BECK TRIB R RIBBL | n/a | n/a | Commissioned in 2018 - full year data expected | 1456.73 | 108 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | LONG STREET COMBINED SEWER OVERFLOW | Long Street CSO (near the Market Place) | 016993581 | ROC0124 | SO | CSO on Sewer Network | SD8704006010 | GB112069061161 | Irk (Sourtce to Wince Brook) | CLVRT'D SECTION THE RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.5 | 4 | 100%
United Utilities | LONGBURGH PUMPING STATION | Longburgh PS | 017670207 | CAR0044 | SO | Storm Discharge at Pumping Station | NY3090059120 | 89 | #N/A | RIDDING SOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 513.24 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LONGFORD BARRAGE CSO 48008 | Longford Barrage CSO | EPRHB3795RH | WAR0016 | SO | CSO on Sewer Network | SJ6038690068 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 250.34 | 33 | 99.86%
United Utilities | LONGRIDGE CSO 343FT | Longridge Combined Sewer Overflow | 017160117 | RIB0028 | SO | CSO on Sewer Network | SD5950036100 | GB112071065470 | Savick Brook | SAVICK BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 32.63 | 21 | 92.51%
United Utilities | LONGSHAW STREET CSO (48066) | Longshaw Street CSO | 016993702 | WAR0066 | SO | CSO on Sewer Network | SJ5989089940 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 165.1 | 26 | 99.95%
United Utilities | LONGTON WASTEWATER TREATMENT WORKS | LONGTON WwTW | 017060019 | 17060019 | ST | Storm Tank at WwTW | SD4687025280 | GB112070064900 | Tarra Carr Gutter | TARRA CARR GUTTER | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 559.4 | 60 | 99.87% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | LONGTOWN WWTW | LONGTOWN WwTW | 017770003 | 17770003 | ST | Storm Tank at WwTW | NY3751068430 | GB102077074190 | Esk (Eden and Esk) | RIVER ESK (BORDER) | N/A | N/A | Commissioned in 2019 - full year data expected | 451.58 | 55 | 99.92% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | LONGTOWN WWTW | LONGTOWN WwTW | 017770003 | 17770003 | SO | Inlet CSO at WwTW | NY3751068430 | GB102077074190 | Esk (Eden and Esk) | RIVER ESK (BORDER) | N/A | N/A | Commissioned in 2019 - full year data expected | 127.91 | 41 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | LONGWORTH RD/R'WAY VIADUCT | Longworth Road/Railway Viaduct CSO | EPRSB3395WA | RIB0021 | SO | CSO on Sewer Network | SD7278036090 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 91.27 | 36 | 96.12%
United Utilities | LORD NORTH STREET/CLIFTON ST CSO | LORD NORTH STREET / CLIFTON STREET CSO | 01MAN0069 | MAN0069 | SO | CSO on Sewer Network | SJ8662099660 | GB112069061152 | Medlock (Lumb Brook to Irwell) | SHOOTERS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 5.97 | 23 | 99.99%
United Utilities | LORD STREET | Lord Street CSO | 016993630 | WIG0053 | SO | CSO on Sewer Network | SD6142003680 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LORDS STREET/FIR STREET CSO | LORDS STREET / FIR STREET CSO | 01SAL0049 | SAL0049 | SO | CSO on Sewer Network | SJ6992092520 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LORDS STREET/LIVERPOOL ROAD CSO | LORDS STREET / LIVERPOOL ROAD CSO | 01SAL0015 | SAL0015 | SO | CSO on Sewer Network | SJ7119091820 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 127.43 | 61 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LORTON STW | LORTON WwTW | 017570046 | 17570046 | SO | Inlet CSO at WwTW | NY1497026450 | GB112075070400 | Cocker - conf Whit Beck to conf Derwent | RIVER COCKER | N/A | N/A | Commissioned in 2020 - full year data expected | 207.08 | 37 | 99.82%
United Utilities | LOSTOCK GROVE CSO | Lostock Grove CSO | 016940193 | TRA0066 | SO | CSO on Sewer Network | SJ7884095310 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 1.13 | 3 | 100%
United Utilities | LOSTOCK JUNCTION LANE CSO | Lostock Junction Lane CSO | 016983108 | BOL0233 | SO | CSO on Sewer Network | SD6732008601 | GB112069064540 | Middle Brook | BESSY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.73%
United Utilities | LOSTOCK ROAD CSO | Lostock Road CSO | NPSWQD010711 | TRA0074 | SO | CSO on Sewer Network | SJ7707095780 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | BENT LANES BROOK VIA SW SEWER | N/A | N/A | Commissioned in 2019 - full year data expected | 208.82 | 70 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LOVERS LANE/LEIGH ROAD CSO (50080) | Lovers Lane/Leigh Road CSO | 016993101 | WIG0200 | SO | CSO on Sewer Network | SD6629002300 | GB112069060810 | Bedford Brook | COLLIER BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.73 | 8 | 100%
United Utilities | LOW BENTHAM WWTW (LOWBE) | LOW BENTHAM WwTW | 017260007 | 17260007 | ST | Storm Tank at WwTW | SD6357069620 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 95.65%
United Utilities | LOW HESKET PS | Low Hesket PS | 017680337 | EDE0088 | SO | Storm Discharge at Pumping Station | NY4636046470 | GB102076074030 | Petteril d/s Blackrack Beck | BARROCK GILL | N/A | N/A | Commissioned in 2019 - full year data expected | 172.56 | 35 | 99.8%
United Utilities | LOW HESKET STW | LOW HESKET WwTW | 017670104 | 17670104 | SO | Inlet CSO at WwTW | NY4603045550 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Commissioned in 2019 - full year data expected | 250.85 | 57 | 99.79% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | LOW MARPLE STW | LOW MARPLE WwTW | 016940178 | 16940178 | ST | Storm Tank at WwTW | SJ9608090500 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Commissioned in 2019 - full year data expected | 1122.5 | 92 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LOW WOOD BRIDGE PUMPING STATION | Low Wood Bridge Pumping Station (Site ID LOWWO) (LAK0054) | 017380340 | LAK0054 | SO | Storm Discharge at Pumping Station | SD3453083680 | GB112073071420 | Leven | RIVER LEVEN | Morcambe Bay (Leven) | N/A | Commissioned in 2016 - full year data expected | 230.24 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LOWCA BROW (PARTON) CSO | Lowca Brow (Parton) CSO | 017470079 | COP0059 | SO | Storm Discharge at Pumping Station | NX9824021200 | GB112074070040 | Lowca Beck | LOWCA BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 154.09 | 77 | 98.38% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LOWCA LANE HAZEL GROVE CSO | Lowca Lane(Hazel Grove) CSO | 017560139 | ALL0068 | SO | CSO on Sewer Network | NY0119030880 | 188 | #N/A | LING BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 201.88 | 52 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LOWE MILL LANE (HINDLEY) CSO | Lowe Mill Lane (Hindley) CSO | NPSWQD006473 | WIG0249 | SO | CSO on Sewer Network | SD6193004410 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 15.65 | 18 | 99.96%
United Utilities | LOWER AUDLEY CSO | Lower Audley Street CSO | 017180646 | BBN0158 | SO | CSO on Sewer Network | SD6847027550 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 96.59%
United Utilities | LOWER BRUNDHURST FARM CSO | Lower Brundhurst Farm CSO | 017190727 | RIB0006 | SO | CSO on Sewer Network | SD6453030530 | GB112071065500 | Ribble - conf Calder to tidal | TRIB OF MELLOR BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 301.23 | 80 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LOWER RD PS | Lower Road PS | 01KNW0007 | KNW0007 | SO | Storm Discharge at Pumping Station | SJ4592085900 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | TRIB DITTON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LOWER TABLEY PUMPING STATION | Lower Tabley PS | 01PRE0079 | PRE0079 | SO | CSO on Sewer Network | SD4987034190 | GB112072065760 | Woodplumpton Brook | WOODPLUMPTON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LOWER WALTON PS | Lower Walton PS & CSO | 016983153 | WAR0004 | SO | Storm Discharge at Pumping Station | SJ6034086380 | 169 | #N/A | RIVER MERSEY | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | LOWER WHARF STREET CSO 442EC | LOWER WHARF STREET CSO | 01TAM0043 | TAM0043 | SO | CSO on Sewer Network | SJ9406098750 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2018 - full year data expected | 161.6 | 83 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LOWER WHARF STREET CSO 442EC | Lower Wharf Street/Scotland Street CSO | 01TAM0043 | TAM0044 | SO | CSO on Sewer Network | SJ9406098750 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2018 - full year data expected | 151.43 | 71 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | LUMB LANE (AUDENSHAW) CSO & DET TNK | Lumb Lane (Audenshaw) CSO and Detention Tank | 016982921 | TAM0170 | SO | Storm Discharge at Pumping Station | SJ9140097501 | GB112069060940 | Micker Brook | CARR BROOK VIA SWS | n/a | n/a | Commissioned in 2019 - full year data expected | 61.63 | 12 | 99.99%
United Utilities | LUMB LANE CSO (432D0) | Lumb Lane CSO | 01STK0016 | STK0016 | SO | CSO on Sewer Network | SJ8921084610 | GB112069060940 | Micker Brook | CARR BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 15.6 | 14 | 100%
United Utilities | LUNE STREET PUMPING STATION 25030 | Lune Street Sewage PS | 017270195 | LAN0007 | SO | Storm Discharge at Pumping Station | SD4757062170 | 178 | #N/A | RIVER LUNE ESTUARINE WATERS | MORECAMBE BAY EAST | Morecambe North | Commissioned in 2016 - full year data expected | 0.54 | 1 | 100%
United Utilities | LYDD GROVE PS | Lydd Grove PS | 017091508 | CHR0038 | SO | Storm Discharge at Pumping Station | SD5701017010 | GB112070064952 | Yarrow DS Big Lodge Water | UNNAMED TRIB OF RIVER CHOR | N/A | N/A | Commissioned in 2019 - full year data expected | 8.73 | 12 | 100%
United Utilities | LYNHOLME RD/OAKDENE RD | Lynholme Road/Oakdene Road | 01LIV0036 | LIV0036 | SO | CSO on Sewer Network | SJ3859096611 | GB112069060600 | Tue Brook | FAZAKERLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LYNTON AVENUE CSO | Lynton Avenue CSO | 01WIG0005 | WIG0005 | SO | CSO on Sewer Network | SD5624006710 | GB112070064820 | Douglas - Lower | CULVERTED TRIB. RIVER DOUGLAS | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | LYTHAM PUMPING STATION | Lytham PS | 017160106 | FYL0003 | SO | Storm Discharge at Pumping Station | SD3835027650 | 176 | #N/A | LIGGARD BROOK | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2016 - full year data expected | 73.66 | 57 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | LYTHAM ROAD | Warton Pumping Station (Site id 19010) (FYL0028) | NPSWQD010748 | FYL0028 | SO | Storm Discharge at Pumping Station | SD3820028200 | GB112071065651 | Main Drain (Ribble) | WREA BROOK | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2017 - full year data expected | 211.74 | 50 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | LYTHAM ROAD CSO (452EF) | LYTHAM ROAD CSO | 01TRA0038 | TRA0038 | SO | CSO on Sewer Network | SJ7314094870 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 53.47 | 31 | 100%
United Utilities | MACCLESFIELD WWTW | MACCLESFIELD WwTW | 016910009 | 16910009 | ST | Storm Tank at WwTW | SJ8961078200 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | MAD HATTER PUB | The Mad Hatter Pub CSO | 016982724 | MAN0290 | SO | CSO on Sewer Network | SJ8725095540 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MADLEY WWTW | MADELEY WwTW | 016810091 | 16810091 | ST | Storm Tank at WwTW | SJ7700045090 | GB112068055200 | Lea | RIVER LEA | N/A | N/A | Commissioned in 2020 - full year data expected | 887.57 | 57 | 100% |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation
United Utilities | MAINWAY/WORCESTER ROAD CSO | Mainway/Worcester Road CSO | 016993575 | ROC0017 | SO | CSO on Sewer Network | SD8649004481 | GB112069061131 | Irk (Wince to Irwell) | BOARDMAN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 130.7 | 34 | 100%
United Utilities | MAINWAYEAST/LINCOLN ROAD CSO | Mainway/Lincoln Road Combined Sewer Overflow | 01ROC0015 | ROC0015 | SO | CSO on Sewer Network | SD8810004590 | GB112069061120 | Wince Brook | WINCE BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 2.37 | 10 | 100%
United Utilities | MALLARD STREET/CHARLES STREET CSO | Mallard Street/Charles Street CSO | 016982736 | MAN0343 | SO | CSO on Sewer Network | SJ8417197501 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.63 | 17 | 100%
United Utilities | MALVERN ROAD CSO (42052) | Malvern Road (St.Helens) CSO | 016982535 | STH0013 | SO | CSO on Sewer Network | SJ5408095850 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 130.11 | 58 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MANC' ROAD (CHAPEL-EN-LE-FRITH) CSO | Manchester Road | 01PEA0048 | PEA0048 | SO | CSO on Sewer Network | SK0504080460 | GB112069060860 | Randall Carr Brook | COMBS RESERVOIR | N/A | N/A | Commissioned in 2019 - full year data expected | 66.43 | 32 | 100%
United Utilities | MANCHESTER NEW ROAD CSO | Manchester New Road Combined Sewer Overflow | 016993577 | ROC0016 | SO | CSO on Sewer Network | SD8649004482 | GB112069061131 | Irk (Wince to Irwell) | BOARDMAN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 3.73 | 12 | 100%
United Utilities | MANCHESTER OLD ROAD CSO | Manchester Old Road CSO | 016982916 | ROC0009 | SO | CSO on Sewer Network | SD8444004740 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.5 | 4 | 99.73%
United Utilities | MANCHESTER RD CSO (351TT) | Manchester Road (Near the Esplanade) CSO | 01ROC0082 | ROC0082 | SO | CSO on Sewer Network | SD8934013200 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | MANCHESTER RD CSO (363F2) | Manchester Road (Bent Street) CSO | 01ROS0038 | ROS0038 | SO | CSO on Sewer Network | SD7937022010 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | CULVERTED LANGWOOD BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.03 | 1 | 96.5%
United Utilities | MANCHESTER RD DALESFORD RD 362EJ | Manchester Road/Dalesford Road | 01ROS0011 | ROS0011 | SO | CSO on Sewer Network | SD7890022521 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RVR IRWELL VIA LANGWOOD BROOK | North Wirral East | N/A | Commissioned in 2019 - full year data expected | 213.5 | 103 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | MANCHESTER RD/HOPE ST | Manchester Road/Hope Street CSO | 016982615 | BOL0199 | SO | CSO on Sewer Network | SD6229009720 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MANCHESTER RD/PARK LANE CSO | Manchester Road/Park Lane CSO | 01WIG0199 | WIG0199 | SO | CSO on Sewer Network | SJ6721099720 | GB112069060810 | Bedford Brook | BEDFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 70.07 | 37 | 100%
United Utilities | MANCHESTER RD/SELBOURNE RD CSO | Manchester Road/Selbourne Road CSO | 01PRE0074 | PRE0074 | SO | CSO on Sewer Network | SD5470028990 | 176 | #N/A | RIVER RIBBLE | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 1.2 | 4 | 92.57%
United Utilities | MANCHESTER ROAD (LOSTOCK) CSO | Manchester Road (Lostock) CSO | EPRSB3399DG | VRY0116 | SO | CSO on Sewer Network | SJ6855074780 | GB112068060390 | Peover Eye | WINCHAM BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.97 | 2 | 100%
United Utilities | MANCHESTER ROAD CSO | Manchester Road CSO | 01TAM0088 | TAM0088 | SO | CSO on Sewer Network | SD9740001660 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MANCHESTER ROAD CSO | Manchester Road CSO | 016982936 | BRY0100 | SO | CSO on Sewer Network | SD8070007730 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 0.53 | 8 | 100%
United Utilities | MANCHESTER ROAD SEWER | Manchester Road Sewer | 01ROS0058 | ROS0058 | SO | CSO on Sewer Network | SD7808023252 | GB112069064650 | Ogden | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MANCHESTER SQUARE PS | Manchester Square PS | 017160287 | BPL0039 | SO | Storm Discharge at Pumping Station | SD3053035070 | GB641211630001 | Mersey Mouth | IRISH SEA | n/a | Blackpool North, Blackpool Central, Blackpool South and Bispham | Commissioned in 2017 - full year data expected | 233.46 | 50 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MANCUNIAN WAY CSO | Mancunian Way CSO | 016982729 | MAN0399 | SO | CSO on Sewer Network | SJ8494097510 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 11.39 | 15 | 99.99%
United Utilities | MANHOLE N20 E PARK DR CSO/SP DR PS | Manhole No. 20 off East Park Drive CSO / South Park Drive PS | 017260025 | BPL0007 | SO | CSO on Sewer Network | SD3290035500 | GB112072066120 | Hillylaid Pool - Tidal Wyre | MARTON MERE VIA MAIN DYKE | N/A | Blackpool North | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | MANHOLE ON SYPHON (WARCOP) CSO | Manhole on Syphon (Warcop) CSO | 01EDE0023 | EDE0023 | SO | CSO on Sewer Network | NY7475015440 | GB102076070750 | Low Gill (Crooks Beck) | CROOKS BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 513.87 | 77 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MANOR AVENUE CSO (45056) | Manor Avenue CSO | 016982887 | TRA0095 | SO | CSO on Sewer Network | SJ7645092841 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 140.37 | 80 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MANOR AVENUE PS | Manor Avenue/Carrington Lane CSO | 016983142 | TRA0043 | SO | CSO on Sewer Network | SJ7636092850 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 45.03 | 40 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MANOR AVENUE PS | Manor Avenue PS | 016983142 | TRA0049 | SO | Storm Discharge at Pumping Station | SJ7636092850 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 102.2 | 22 | 99.9%
United Utilities | MANOR AVENUE/FIRS ROAD CSO | Manor Avenue/Firs Road CSO | 016892365 | TRA0006 | SO | CSO on Sewer Network | SJ7646092840 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 11.2 | 9 | 100%
United Utilities | MANOR HOUSE LANE CSO 33037 | Manor House Lane CSO | 017180627 | PRE0069 | SO | CSO on Sewer Network | SD5531031490 | GB112071065470 | Savick Brook | EAVES BK, TRIB OF SAVICK BK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | MANOR ROAD CSO (052ER) | MANOR ROAD CSO | 01BBN0068 | BBN0068 | SO | CSO on Sewer Network | SD6701027830 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0.43 | 3 | 100%
United Utilities | MANOR ROAD PUMPING STATION | Manor Road PS | 016942050 | STK0042 | SO | Storm Discharge at Pumping Station | SJ9366092450 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 33.47 | 13 | 99.99%
United Utilities | MANOR STREET BOW STREET CSO 072ES | MANOR STREET / BOW STREET CSO | 01BOL0122 | BOL0122 | SO | CSO on Sewer Network | SD7187009410 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Commissioned in 2018 - full year data expected | 0.47 | 2 | 100%
United Utilities | MANORA ROAD (DANE NURSERIES) CSO | Manora Road (Dane Nurseries) CSO | 016881776 | VRY0078 | SO | CSO on Sewer Network | SJ6613073480 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE | N/A | N/A | Commissioned in 2019 - full year data expected | 119.36 | 66 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MANSHAW ROAD CSO | Manshaw Road CSO | 016982836 | TAM0174 | SO | CSO on Sewer Network | SJ9014397126 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MOSS BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 39.54 | 13 | 99.71% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | MAPLE AVENUE CSO | Maple Avenue CSO | 01BRY0086 | BRY0086 | SO | CSO on Sewer Network | SD8072004880 | GB112069061451 | Irwell (Croal to Irk) | TRIB BRADLEY BROOK SUF WTR SEW | N/A | N/A | Commissioned in 2018 - full year data expected | 7.1 | 21 | 100%
United Utilities | MARKET STREET/TRINITY STREET CSO | MARKET STREET / TRINITY STREET CSO | 01TAM0100 | TAM0100 | SO | CSO on Sewer Network | SJ9635098600 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MARLAND HILL SSO | Marland Hill SSO | 01ROC0157 | ROC0157 | SO | CSO on Sewer Network | SD8819012282 | GB112069064600 | Roch (Spodden to Irwell) | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MARLOWE ROAD (PLAYING FIELDS) CSO | Marlowe Road (Playing Fields) CSO | 01VRY0080 | VRY0080 | SO | CSO on Sewer Network | SJ6704072970 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE | N/A | N/A | Commissioned in 2020 - full year data expected | 433.11 | 93 | 99.78% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MARPLE ROAD COMBINED SEWER OVERFLOW | Marple Road CSO | 016982662 | STK0096 | SO | CSO on Sewer Network | SJ9266088870 | GB112069060950 | Poise Brook | POISE BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 94.33 | 33 | 100%
United Utilities | MARSH LANE CSO PRE0021 | Marsh Lane CSO | 017190874 | PRE0021 | SO | CSO on Sewer Network | SD5269129413 | 176 | #N/A | RIVER RIBBLE VIA CHAIN CULVERT | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | MARTON NORTH WWTW | MARTON NORTH (Cassia) WwTW | 016810093 | 16810093 | SO | Inlet CSO at WwTW | SJ6205067880 | GB112068060540 | Bogart Brook | BOGART BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MARYLAND LANE CSO | Maryland Lane CSO | 016892463 | WIR0148 | SO | CSO on Sewer Network | SJ2477090370 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | NORTH WIRRAL (WEST) | Moreton | Commissioned in 2016 - full year data expected | 0.27 | 5 | 100%
United Utilities | MARYPORT SEWAGE PUMPING STATION | Maryport Sewage PS | 017580242 | ALL0122 | SO | Storm Discharge at Pumping Station | NY0299036090 | 357 | #N/A | IRISH SEA | Silloth | Allonby South and Allonby West Winds | Commissioned in 2017 - full year data expected | 180.74 | 18 | 100%
United Utilities | MATHER AVE ALBERT AVE CSO | Mather Avenue/Albert Avenue CSO | 016950319 | BRY0082 | SO | CSO on Sewer Network | SD8218002340 | GB112069061451 | Irwell (Croal to Irk) | SINGLETON BROOK TRIB R IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 2.67 | 12 | 100%
United Utilities | MATHER LANE | Mather Lane CSO | 01WIG0080 | WIG0080 | SO | CSO on Sewer Network | SJ6581099001 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MAULDETH ROAD CSO | Mauldeth Road CSO | 016993515 | MAN0229 | SO | CSO on Sewer Network | SJ8302093530 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 68.07 | 33 | 100%
United Utilities | MAULDETH ROAD WEST CSO (28043) | Mauldeth Road West CSO | 01MAN0230 | MAN0230 | SO | CSO on Sewer Network | SJ8340093650 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK VIA CULVERT | N/A | N/A | Commissioned in 2020 - full year data expected | 278.93 | 52 | 97.41% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MAVIS DRIVE | Mavis Drive CSO | 01CHR0006 | CHR0006 | SO | CSO on Sewer Network | SD5616014660 | GB112070064952 | Yarrow DS Big Lodge Water | CLANCUTT BROOK | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | MAYFIELD DRIVE PS1 CSO 512EZ | Mayfield Drive PS1 CSO (512EZ) | 01WIR0108 | WIR0108 | SO | CSO on Sewer Network | SJ3650081801 | 171 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 0 | 0 | 99.99% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | MAYFIELDS DRIVE WW NTWK PS | Mayfield Drive Ww Ntwk PS | 01WIR0109 | WIR0109 | SO | Storm Discharge at Pumping Station | SJ3650081802 | 171 | #N/A | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MEADOW LANE COMBINED SEWER OVERFLOW | Meadow Lane CSO | 01TAM0002 | TAM0002 | SO | CSO on Sewer Network | SJ9338293069 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 372.26 | 94 | 99.18% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | MEADOW RD CSO 023A8 | Meadow Road CSO | 017480432 | COP0045 | SO | CSO on Sewer Network | NX9803015661 | 356 | #N/A | POW BECK | n/a | n/a | Commissioned in 2017 - full year data expected | 100.13 | 29 | 100%
United Utilities | MEADOWBANK/BRADFORD RD PS | Meadowbank/Bradford Road PS | 016881775 | VRY0142 | SO | Storm Discharge at Pumping Station | SJ6530068270 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 498.86 | 66 | 99.23% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MEADOWFIELD GOSFORTH CSO | Meadowfield Gosforth Combined Sewer Overflow (Site ID 02631) (COP0030) | 01COP0030 | COP0030 | SO | CSO on Sewer Network | NY0685003370 | GB112074070090 | Bleng | ESK | N/A | Seascale | Commissioned in 2016 - full year data expected | 2.11 | 6 | 99.99%
United Utilities | MEATHOP PUMPING STATION | Meathop PS | 017380417 | LAK0102 | SO | Storm Discharge at Pumping Station | SD4415080530 | 183 | #N/A | MEATHOP MARSH DRAIN | N/A | N/A | Commissioned in 2019 - full year data expected | 167.67 | 20 | 98.72%
United Utilities | MEDLOCK SPORTS CENTRE CSO | Medlock Sports Centre CSO | 016983275 | TAM0005 | SO | CSO on Sewer Network | SJ9049199291 | GB112069061151 | Medlock (Source to Lumb Brook) | LUMB BROOK VIA SURFACE WTR SEW | n/a | n/a | Commissioned in 2018 - full year data expected | 3.52 | 6 | 99.98%
United Utilities | MEETING HOUSE LANE CSO | Meeting House Lane CSO | 017580314 | ALL0009 | SO | CSO on Sewer Network | NY2535048600 | GB102075073390 | Wiza Beck | WIZA BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 148.53 | 52 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MELANDRA ROAD PS | Melandra Road PS | 016982612 | PEA0081 | SO | Storm Discharge at Pumping Station | SK0101095240 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | GLOSSOP BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | MELBOURNE PARK CSO | MELBOURNE PARK CSO | 017680278 | CAR0058 | SO | CSO on Sewer Network | NY4159055340 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | Solway | N/A | Commissioned in 2018 - full year data expected | 38.9 | 12 | 100%
United Utilities | MELBOURNE STREET | Melbourne Street CSO | 016993731 | TAM0105 | SO | CSO on Sewer Network | SJ9628098530 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | THE RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MELBOURNE STREET/WATER STREET CSO | MELBOURNE STREET / WATER STREET CSO | 01HYN0034 | HYN0034 | SO | CSO on Sewer Network | SD7621028760 | GB112071065040 | Hyndburn | CULVERTED TRIB RIVER HYNDBURN | N/A | N/A | Commissioned in 2019 - full year data expected | 2.67 | 9 | 100%
United Utilities | MELBOURNE TERRACE CSO | Melbourne Terrace CSO | 01ALL0089 | ALL0089 | SO | CSO on Sewer Network | NX9957025470 | 356 | #N/A | UNNAMED TRIB OF RIVER WYRE | n/a | n/a | Commissioned in 2018 - full year data expected | 4.8 | 18 | 100%
United Utilities | MELLING WWTW | MELLING WwTW | 016987034 | 16987034 | SO | Inlet CSO at WwTW | SJ3895098900 | GB112069061441 | Alt US Bull Bridge | UNNAMED TRIB OF RIVER ALT | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.97%
United Utilities | MELLOR STREET CSO | MELLOR STREET CSO | 01ROC0029 | ROC0029 | SO | CSO on Sewer Network | SD8860013800 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0.1 | 1 | 99.91%
United Utilities | MELMERBY STW | MELMERBY WwTW | 017670068 | 17670068 | SO | Inlet CSO at WwTW | NY6010037660 | GB102076073810 | Robberby Water | MELMERBY (DALE) BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 41.93 | 17 | 99.89%
United Utilities | MERCHANTS LANDING CULVERT ST CSO | Merchants Landing (Culvert Street) CSO | 01BBN0056 | BBN0056 | SO | CSO on Sewer Network | SD6877027450 | GB112071065310 | Blakewater | CULVERT CULVERT ST | N/A | N/A | Commissioned in 2019 - full year data expected | 38.13 | 6 | 100%
United Utilities | MERE BROW WWTW | MERE BROW WwTW | 017030002 | 17030002 | ST | Storm Tank at WwTW | SD4240018870 | GB112070064880 | Back Drain and Sluice | TARLETON RUNNER | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 2262.36 | 174 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | MERE BROW WWTW | MERE BROW WwTW | 017030002 | 17030002 | SO | Inlet CSO at WwTW | SD4240018870 | GB112070064880 | Back Drain and Sluice | TARLETON RUNNER | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 150.91 | 22 | 99.98%
United Utilities | MERE DRIVE / RAKE LANE CSO (374Y5) | Mere Drive/Rake Lane CSO | 016993604 | SAL0109 | SO | CSO on Sewer Network | SD7916001880 | GB112069061451 | Irwell (Croal to Irk) | SLACK BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 79.93 | 85 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MERE HEATH PUMPING STATION | Mere Heath PS | 016881958 | VRY0018 | SO | Storm Discharge at Pumping Station | SJ6659069880 | GB112068060470 | Dane (Wheelock to Weaver) | PECKMILL BK (TRIB OF R.DANE) | N/A | N/A | Commissioned in 2020 - full year data expected | 103.12 | 13 | 100%
United Utilities | MERSEY ROAD COMBINED SEWER OVERFLOW | Mersey Road CSO | 016930983 | LIV0052 | SO | CSO on Sewer Network | SJ3808085270 | 167 | #N/A | MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 50.27 | 34 | 100%
United Utilities | MERSEY VIEW ROAD CSO | Pickering Pasture SSO | EPRQB3792VW | HAL0118 | SO | CSO on Sewer Network | SJ4888083420 | 167 | #N/A | THE MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 559.87 | 81 | 98.26% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | MH 63 EAST END OF COPSTER GREEN CSO | M/H 63 East End of Copster Green CSO | EPRSB3396AJ | RIB0047 | SO | CSO on Sewer Network | SD6815034230 | GB112071065710 | Showley Brook | TRIB OF DINCKLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 733.73 | 104 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MH Y6 HAVELOCK ROAD CSO | MH Y6 Havelock Road CSO | 017060092 | SRI0006 | SO | CSO on Sewer Network | SD5615025440 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 5.83 | 6 | 100%
United Utilities | MICKLE TRAFFORD PUMPING STATION | Mickle Trafford PS | 016892313 | CHE0028 | SO | Storm Discharge at Pumping Station | SJ4408070700 | GB112068060260 | Stanney Mill Brook | TRIB OF STANNEY MILL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 218.39 | 51 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MICKLE TRAFFORD PUMPING STATION | Mickle Trafford PS | 016892313 | CHE0028 | SO | Storm Discharge at Pumping Station | SJ4408070700 | GB112068060260 | Stanney Mill Brook | TRIB OF STANNEY MILL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 99.98%
United Utilities | MIDDLE POOL PS MIDDP LAN0099 | Middle Pool Pumping Station (Site ID MIDDP) (LAN0099) | 017280289 | LAN0099 | SO | Storm Discharge at Pumping Station | SD4348058330 | GB112072065950 | Overton Dyke | LADES POOL | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | MIDDLETON MAIN OUTFALL | MIDDLETON MAIN OUTFALL CSO | 016982643 | ROC0167 | SO | CSO on Sewer Network | SD8558005230 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 248.6 | 72 | 99.69% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MIDDLETON OLD ROAD CSO | Middleton Old Road CSO (Site ID - 28064/28CSO143) | NPSWQD010702 | MAN0135 | SO | CSO on Sewer Network | SD8541002230 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 500.5 | 93 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MIDDLETON OVERTON WWTW MIDDL | MIDDLETON/OVERTON WwTW | 017270051 | 17270051 | ST | Storm Tank at WwTW | SD4304057960 | 343 | #N/A | LADES POOL ESTUARINE WATERS | LUNE (BROADFLEET) | Morecambe South Morecambe North | Commissioned in 2016 - full year data expected | 34.76 | 6 | 99.94%
United Utilities | MIDDLETON RD PS | Middleton Road PS | 016982942 | ROC0184 | SO | Storm Discharge at Pumping Station | SD8638008750 | GB112069061250 | Whittle Brook (Irwell) | WHITTLE BROOK | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | MIDDLETON ROAD CSO | Middleton Road (Heywood) CSO | NPSWQD010709 | ROC0033 | SO | CSO on Sewer Network | SD8635009120 | GB112069061250 | Whittle Brook (Irwell) | WHITTLE BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0.23 | 3 | 100%
United Utilities | MIDDLETON ROAD/VICTORIA AVENUE CSO | MIDDLETON ROAD / VICTORIA AVENUE CSO | 01MAN0096 | MAN0096 | SO | CSO on Sewer Network | SD8386004060 | GB112069061131 | Irk (Wince to Irwell) | TRIBUTARY OF RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 282 | 78 | 92.6% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MIDDLEWICH RD/PARKFIELD RD CSO | Middlewich Road/Parkfield Road CSO | 016892279 | VRY0094 | SO | CSO on Sewer Network | SJ6697079240 | GB112068060420 | Arley Brook (Source to Gale Brook) | RIVER DANE VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 234.3 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | MIDDLEWICH ROAD CSO 131AD | Middlewich Road CSO | 01CON0003 | CON0003 | SO | CSO on Sewer Network | SJ7469060160 | GB112068055420 | Wheelock (including Hassall Brook) | UNNAMED TRIB RIVER WHEELOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 28.57 | 16 | 100%
United Utilities | MILL BROW/BLACKLEY NEW ROAD CSO | Mill Brow/Blackley Road CSO | 016982717 | MAN0112 | SO | CSO on Sewer Network | SD8520502856 | GB112069061131 | Irk (Wince to Irwell) | A CULVERTED SECTION RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 21.37 | 26 | 84.19% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | MILL BROW/BLACKLEY NEW ROAD CSO | Mill Brow/Blackley New Road CSO | 016993671 | MAN0269 | SO | CSO on Sewer Network | SD8520502856 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED TRIB OF RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 11.93 | 20 | 100%
United Utilities | MILL COTTAGES CSO | MILL COTTAGES CSO | 01COP0024 | COP0024 | SO | CSO on Sewer Network | NY0092023860 | GB112074070040 | Lowca Beck | DISTINGTON BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MILL HILL LANE CSO 132F8 | MILL HILL LANE CSO | 01CON0045 | CON0045 | SO | CSO on Sewer Network | SJ7536059830 | GB112068055430 | Arclid Brook | RIVER WHEELOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 18.9 | 23 | 94.53%
United Utilities | MILL HOUSE LANE CSO | Mill House Lane CSO | 016982895 | WAR0117 | SO | CSO on Sewer Network | SJ6392092570 | GB112069061020 | Spittle Brook | TRIB COCK SHOT BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 203.67 | 55 | 97.8% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILL LANE (GOLBORNE) CSO | Mill Lane (Golborne) CSO | 016983354 | WIG0147 | SO | CSO on Sewer Network | SJ6060097290 | GB112068055360 | Biddulph Brook | DANE-IN-SHAW BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1648.22 | 97 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILL LANE CEMETERY CSO | Mill Lane Cemetery CSO | 01STK0128 | STK0128 | SO | CSO on Sewer Network | SJ8585089200 | GB112069060940 | Micker Brook | CHORLTON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 49.7 | 22 | 99.99%
United Utilities | MILL LANE COMBINED SEWER OVERFLOW | Mill Lane CSO | 016982772 | TAM0163 | SO | CSO on Sewer Network | SJ9406094780 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 3.39 | 9 | 100%
United Utilities | MILL LANE CSO (134I5) | MILL LANE CSO | 01CON0035 | CON0035 | SO | CSO on Sewer Network | SJ8837061520 | GB112068055360 | Biddulph Brook | DANE-IN-SHAW BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 154.47 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILL LANE CSO 425E6 | Mill Lane CSO | 01STH0049 | STH0049 | SO | CSO on Sewer Network | SJ8837061520 | GB112068055360 | Biddulph Brook | DANE-IN-SHAW BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 59.83 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILL LANE CSO 49201 | Mill Lane CSO | 017091498 | WIG0164 | SO | CSO on Sewer Network | SJ8837061520 | GB112068055360 | Biddulph Brook | DANE-IN-SHAW BROOK | n/a | n/a | Commissioned in 2020 - full year data expected | 727.58 | 115 | 50.41% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILL LANE LEIGH CSO 50079 | Mill Lane (Leigh) CSO | 01WIG0198 | WIG0198 | SO | CSO on Sewer Network | SJ6690099950 | GB112069060810 | Bedford Brook | BEDFORD BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 60.53 | 31 | 99.99%
United Utilities | MILL LANE PS | 95 Mill Lane (St.Helens) CSO | 016990476 | STH0065 | SO | CSO on Sewer Network | SJ9050093500 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 0.4 | 2 | 92.67%
United Utilities | MILL LANE/WINWICK RD SSO | Junction of Mill Lane & Winwick Road CSO | 016920072 | WAR0018 | SO | CSO on Sewer Network | SJ6017091370 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | MILL BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 128.36 | 23 | 100%
United Utilities | MILL STREET BRADFORD MANCHESTER CSO | Mill Street CSO | 016982733 | MAN0320 | SO | CSO on Sewer Network | SJ7066055300 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0.43 | 1 | 100%
United Utilities | MILL STREET CSO CREWE 169CW | MILL STREET CSO | 01CRE0042 | CRE0042 | SO | CSO on Sewer Network | SJ7066055300 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | MILLER STREET/CORPORATION ST CSO | Miller St/Corporation St CSO | 01MAN0161 | MAN0161 | SO | CSO on Sewer Network | SJ8414099060 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MILLERS BRIDGE CSO 99004 | Millers Bridge CSO | 016931015 | SEF0108 | SO | CSO on Sewer Network | SJ3300094300 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 27.13 | 4 | 100%
United Utilities | MILLGATE CSO 35025 | Millgate CSO | 01ROC0072 | ROC0072 | SO | CSO on Sewer Network | SD9116014680 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 295.93 | 82 | 98.26% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILLOM WASTEWATER TREATMENT WORKS | MILLOM WwTW | 017470048 | 17470048 | ST | Storm Tank at WwTW | SD1922079410 | 344 | #N/A | DUDDON ESTUARY | Duddon and Walney | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 0.98 | 1 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | MILNROW ROAD/FISHWICK STREET CSO | Milnrow Road CSO | 016993541 | ROC0103 | SO | CSO on Sewer Network | SD9050012920 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 258.92 | 88 | 97.31% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILNROW ROAD/FISHWICK STREET CSO | Milnrow Road/Fishwick Street CSO | 016993541 | ROC0027 | SO | CSO on Sewer Network | SD9050012920 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0.23 | 1 | 100%
United Utilities | MILNROW ROAD/PINE STREET CSO | Milnrow Road/Pine Street | EPRSB3396VR | ROC0091 | SO | CSO on Sewer Network | SD9050013260 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 99.99%
United Utilities | MILNTHORPE SEWAGE PS MLNTH | Milnthorpe Sewage PS | 017380339 | LAK0052 | SO | Storm Discharge at Pumping Station | SD4939081400 | GB112073071070 | Bela | RIVER BELA | MORECAMBE BAY EAST | N/A | Commissioned in 2018 - full year data expected | 1808.89 | 96 | 99.78% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MILTON PUMPING STATION | Milton East WW Net PS | 017680328 | CAR0083 | SO | Storm Discharge at Pumping Station | NY5533060550 | GB102076074050 | Quarry Beck | MILTON BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 100.75 | 21 | 99.96%
United Utilities | MILTON PUMPING STATION | Cumcatch (Milton West) PS | 017680328 | CAR0075 | SO | Storm Discharge at Pumping Station | NY5533060550 | GB102076074050 | Quarry Beck | MILTON BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 4.16 | 3 | 99.95%
United Utilities | MILVERTON AVENUE | Hattersley SSO | 01TAM0148 | TAM0148 | SO | CSO on Sewer Network | SJ9717094480 | GB112069061280 | Wilson Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MOBBERLEY RD CSO | Mobberley Road Combined Sewer Overflow (Site ID 272GZ) (MAC0122) | 016892553 | MAC0122 | SO | CSO on Sewer Network | SJ7684079530 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | BIRKIN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 79.17 | 54 | 92.43% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | MOBBERLEY WWTW | MOBBERLEY WwTW | 016910010 | 16910010 | SO | Inlet CSO at WwTW | SJ7834080290 | GB112069061330 | Mobberley Brook | MOBBERLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | MOBBERLEY WWTW | MOBBERLEY WwTW | 016910010 | 16910010 | ST | Storm Tank at WwTW | SJ7834080290 | GB112069061330 | Mobberley Brook | MOBBERLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 2635.97 | 146 | 78.67% | Sensor failure / issue | Resolved - October | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | MOLYNEUX DRIVE CSO 24009 | Molyneux Drive CSO | 016993826 | KNW0021 | SO | CSO on Sewer Network | SJ4581090940 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | PRESCOT BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 86.28 | 62 | 99.91% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MONSALL ROAD (J SEWER) CSO (282SF) | MONSALL ROAD (J SEWER) CSO | 01MAN0086 | MAN0086 | SO | CSO on Sewer Network | SD8613400952 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED TRIB OF MOSTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.6 | 14 | 100%
United Utilities | MOOR ROAD EAVES GREEN RD CSO 122GB | Moor Road/Eaves Green Road CSO | 017081255 | CHR0087 | SO | CSO on Sewer Network | SD5683015941 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | n/a | n/a | Commissioned in 2018 - full year data expected | 72.23 | 76 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | MOOR ROAD EAVES GREEN RD CSO 122GB | Moor Row CSO | 017081255 | COP0090 | SO | CSO on Sewer Network | SD5683015941 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | N/A | St Bees | Commissioned in 2018 - full year data expected | 296.1 | 76 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | MOORBROOK STREET CSO 332F2 | MOORBROOK STREET CSO | PRE0023 | PRE0023 | SO | CSO on Sewer Network | SD5354930499 | 176 | #N/A | CLVRT MOOR BROOK TRIB RVR RIBB | N/A | N/A | Commissioned in 2018 - full year data expected | 93.03 | 25 | 99.99%
United Utilities | MOORFILED HALL CSO 432G4 | Moorfield Hall CSO | 016982981 | STK0141 | SO | CSO on Sewer Network | SJ8845083800 | GB112069061360 | Dean (Bollington to Bollin) | TRIB SPATH BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 438.8 | 65 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MORECAMBE BANK CSO | Morecambe Bank CSO | 01LAK0071 | LAK0071 | SO | CSO on Sewer Network | SD4087077860 | 184 | #N/A | KENT CHANNEL | MORECAMBE BAY EAST | N/A | Commissioned in 2018 - full year data expected | 0.83 | 2 | 100%
United Utilities | MORESBY PARKS PS | Moresby Park PS | 017470124 | COP0073 | SO | Storm Discharge at Pumping Station | NY0031018540 | GB112074070030 | Keekle (upper) | BLACKWOOD BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 2.25 | 5 | 100% |  |  |  |  | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | MORICAMBE PARK PS 02540 | Moricambe Park PS | 017580248 | ALL0111 | SO | Storm Discharge at Pumping Station | NY1282055840 | 90 | #N/A | GREAT GUTTER ESTUARINE WATER | SILLOTH | Silloth | Commissioned in 2016 - full year data expected | 2.57 | 1 | 100%
United Utilities | MORLAND WASTEWATER TREATMENT WORKS | MORLAND WwTW | 017670019 | 17670019 | SO | Inlet CSO at WwTW | NY5974022750 | GB102076070830 | Morland Beck | MORLAND BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 1875.25 | 315 | 99.92% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | MORNINGTON RD BACK LINCOLN RD CSO | Mornington Road/Back Lincoln Road CSO | 01BOL0117 | BOL0117 | SO | CSO on Sewer Network | SD7001009390 | GB112069064540 | Middle Brook | QUEENS PARK GILNOW PARK POND | N/A | N/A | Commissioned in 2018 - full year data expected | 3.63 | 7 | 100%
United Utilities | MORRIS STREET CSO (BRY0137) | Morris Street CSO | EPRJB3893EY | BRY0137 | SO | CSO on Sewer Network | SD8009308224 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MORTAR PITS COMBINED SEWER OVERFLOW | Mortar Pits CSO | 017290473 | LAK0060 | SO | CSO on Sewer Network | SD6624091740 | GB112072071710 | Rawthey - Lower | RIVER RAWTHEY | N/A | N/A | Commissioned in 2019 - full year data expected | 8.63 | 14 | 100%
United Utilities | MOSS BANK WAY/CHIPPINGS W | Moss Bank Way/Chippings Road CSO | 01BOL0077 | BOL0077 | SO | CSO on Sewer Network | SD6894010890 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MOSS LANE ACRE LANE CSO 431AM | Moss Lane/Acre Lane CSO | 01STK0010 | STK0010 | SO | CSO on Sewer Network | SJ8905084711 | GB112069060940 | Micker Brook | CARR BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 9.47 | 12 | 100%
United Utilities | MOSS LANE COMBINED SEWER OVERFLOW | Moss Lane CSO | EPRRB3090NV | WAR0124 | SO | CSO on Sewer Network | SJ6750296050 | GB112069061420 | Glaze | GLAZE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 160.86 | 30 | 99.99%
United Utilities | MOSS LANE SANDBACH 138CF | MOSS LANE CSO | 01CON0049 | CON0049 | SO | CSO on Sewer Network | SJ7329060960 | GB112068055420 | Wheelock (including Hassall Brook) | TRENT AND MERSEY CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 908.93 | 83 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | MOSS NOOK PS | Watery Lane PS CSO | 016982541 | PRE0036 | SO | CSO on Sewer Network | SJ5340094400 | GB112069061170 | Sutton Brook | SUTTON BROOK | N/A | St Annes | Commissioned in 2016 - full year data expected | 0.7 | 2 | 99.99%
United Utilities | MOSSLEY STW | MOSSLEY WwTW | 016940089 | 16940089 | ST | Storm Tank at WwTW | SD9732000880 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | MOSSLEY STW | MOSSLEY WwTW | 016940089 | 16940089 | SO | Inlet CSO at WwTW | SD9732000880 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | MOSSWAY CSO | Mossway CSO | 016982901 | ROC0185 | SO | CSO on Sewer Network | SD8686003920 | GB112069061131 | Irk (Wince to Irwell) | BOARDMAN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | MOSTON LANE/ROCHDALE ROAD CSO | Moston Lane/Rochdale Road CSO | NPSWQD010701 | MAN0123 | SO | CSO on Sewer Network | SD8542001800 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 111.87 | 48 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MOSTON RD/ CHADDERTON LOW LEVEL PS | Moston Road Combined Sewer Overflow/Chadderton Low Level Pumping Station (318N4) (OLD0157) | 016983361 | OLD0157 | SO | Storm Discharge at Pumping Station | SD8869004570 | GB112069061120 | Wince Brook | WINCE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 106.27 | 49 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | MOTHERBY WASTEWATER TREATMENT WORKS | MOTHERBY WwTW | 017670105 | 17670105 | SO | Inlet CSO at WwTW | NY4322028690 | GB102076073992 | Petteril u/s M6 | RIVER PETTERIL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MOUNT ROAD COMBINED SEWER OVERFLOW | Mount Road CSO | 01MAN0246 | MAN0246 | SO | CSO on Sewer Network | SJ8807095271 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 20.43 | 16 | 96.54%
United Utilities | MOUNT SION ROAD CSO | Mount Sion Road | 01BRY0037 | BRY0037 | SO | CSO on Sewer Network | SD7738006470 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MOUNT STREET/GREEK STREET CSO | MOUNT STREET / GREEK STREET CSO | 01MAN0187 | MAN0187 | SO | CSO on Sewer Network | SJ8453097390 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 1.03 | 4 | 100%
United Utilities | MOUSLEY BOTTOM PS | Mousley Bottom PS | 016982820 | PEA0086 | SO | Storm Discharge at Pumping Station | SJ9930085200 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Commissioned in 2019 - full year data expected | 0.22 | 1 | 100%
United Utilities | MOWBRECK WW NTWK PS | Mowbreck Ww Ntwk PS | 01FYL0036 | FYL0036 | SO | Storm Discharge at Pumping Station | SD4270033200 | GB112071065670 | Dow Brook | UNNAMED TRIB OF CARR BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | MURTON BRIDGE HOUSE PUMPING STATION | Murton (Bridge House) PS | 017680533 | EDE0114 | SO | Storm Discharge at Pumping Station | NY7275121661 | GB102076070850 | Trout Beck (Murton) | MURTON BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 3.91 | 4 | 99.55%
United Utilities | MURTON WASTEWATER TREATMENT WORKS | MURTON WwTW | 017680532 | 17680532 | SO | Inlet CSO at WwTW | NY7234021670 | GB102076070850 | Trout Beck (Murton) | MURTON BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 332.16 | 56 | 99.56% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | NANTWICH ROAD CHESTER RD CSO 131J6 | Chester Road (Middlewich) WwNPS | 01CON0010 | CON0010 | SO | Storm Discharge at Pumping Station | SJ6947066690 | GB112068055380 | Wheelock (Fowle Brook to Dane) | 0 | N/A | N/A | Commissioned in 2020 - full year data expected | 142.75 | 53 | 99.69% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NANTWICH ROAD CHESTER RD CSO 131J6 | Nantwich Road/Chester Road CSO | 01CON0009 | CON0009 | SO | CSO on Sewer Network | SJ6947066690 | GB112068055380 | Wheelock (Fowle Brook to Dane) | RIVER WHEELOCK | N/A | N/A | Commissioned in 2018 - full year data expected | 40.53 | 12 | 100%
United Utilities | NAVIGATION ROAD CSO (472HN) | Navigation Road (Northwich) CSO | 01VRY0068 | VRY0068 | SO | CSO on Sewer Network | SJ6557073230 | GB112068060460 | Weaver (Marbury Brook to Dane) | WEAVER NAVIGATION | N/A | N/A | Commissioned in 2020 - full year data expected | 105.57 | 77 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NAZE LANE PUMPING STATION | Naze Lane PS (19048) | 017180397 | FYL0018 | SO | Storm Discharge at Pumping Station | SD4233027040 | 176 | #N/A | POOL STREAM | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 1231.23 | 92 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NE AREA SEWER | Thursby Road/Basnett Street | 017160194 | BUR0002 | SO | CSO on Sewer Network | SD8514033610 | GB112071065100 | Brun - conf Don to conf Calder | RIVER BURN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | NEAR BUTTS BECK CSO (321H7) | Near Butts Beck Footpath CSO | 01PEN0025 | PEN0025 | SO | CSO on Sewer Network | SD8756046820 | GB112071065540 | Stock Beck | BUTTS BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.43 | 7 | 100%
United Utilities | NEAR SAWREY WWTW NEARS | NEAR SAWREY WwTW | 017370030 | 17370030 | SO | Inlet CSO at WwTW | SD3660095110 | GB112073071400 | Cunsey Beck/Black Beck | CUNSEY BECK | N/A | Windermere, Millerground Landing | Commissioned in 2016 - full year data expected | 1459.36 | 82 | 98.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | NEAR SHIP INN CSO | Near the Ship Inn CSO | 017190859 | FYL0016 | SO | CSO on Sewer Network | SD4360028701 | GB112071065670 | Dow Brook | DOW BROOK TRIB OF FRECKLTON PL | n/a | n/a | Commissioned in 2018 - full year data expected | 110.67 | 31 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | NEAR TAWD VALE INN CSO | Near Tawd Vale Inn | EPRSB3399WS | WLN0027 | SO | CSO on Sewer Network | SD4810006990 | GB112070064790 | Tawd | RIVER TAWD VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 138.8 | 50 | 94.22% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NETHER KELLET WTW NETHK | NETHER KELLET WwTW | 017370074 | 17370074 | ST | Storm Tank at WwTW | SD5018068160 | 185 | #N/A | NETHER BECK, TRIB RIVER KEER | MORECAMBE BAY EAST | N/A | Commissioned in 2018 - full year data expected | 1031.22 | 74 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NETHER PEOVER STW | NETHER PEOVER WwTW | 016810098 | 16810098 | ST | Storm Tank at WwTW | SJ7340573665 | GB112068060390 | Peover Eye | TRIB CROW BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1592.07 | 139 | 99.71% |  |  | Performance - Other maintenance / capital works (e.g. jetting)
United Utilities | NETHERFIELD ROAD CSO (32019) | Netherfield Road CSO | 017180620 | PEN0083 | SO | CSO on Sewer Network | SD8619037550 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Commissioned in 2020 - full year data expected | 103.92 | 61 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | NEW BRIGHTON PUMPING STATION | New Brighton PS | 016810340 | WIR0130 | SO | Storm Discharge at Pumping Station | SJ3140094200 | 171 | #N/A | TIDAL RIVER MERSEY | North Wirrall (East) and North Wirrall (West) | Moreton and Wallasey | Commissioned in 2017 - full year data expected | 0.07 | 1 | 100%
United Utilities | NEW HALL HEY BRIDGE CSO | New Hall Hey Bridge CSO | 016982933 | ROS0075 | SO | CSO on Sewer Network | SD8095022410 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Commissioned in 2020 - full year data expected | 481.13 | 93 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEW HALL HEY ROAD CSO | New Hall Hey Road CSO | 016993908 | ROS0009 | SO | CSO on Sewer Network | SD8013022050 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 18.91 | 10 | 99.88%
United Utilities | NEW MILL STREET CSO | New Mill Street CSO | EPRWP3723XP | BBN0168 | SO | CSO on Sewer Network | SD6871828831 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 5.2 | 7 | 99.99%
United Utilities | NEW STREET COMBINED SEWER OVERFLOW | NEW STREET CSO | 01BRY0008 | BRY0008 | SO | CSO on Sewer Network | SD7779012790 | GB112069064610 | Kirklees Brook | BLACK BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 3844.87 | 234 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEWBIGGIN (LEVEN) WWTW NEWBG | NEWBIGGIN WwTW | 017370051 | 17370051 | ST | Storm Tank at WwTW | SD2675168941 | GB112073071150 | Deep Meadows Beck | DEEP MEADOWS BECK | Morecambe Bay (Leven) and Roose Beck | n/a | Commissioned in 2017 - full year data expected | 3877.88 | 176 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEWBIGGIN (LEVEN) WWTW NEWBG | NEWBIGGIN WwTW | 017370051 | 17370051 | ST | Storm Tank at WwTW | SD2675168941 | GB112073071150 | Deep Meadows Beck | DEEP MEADOWS BECK | Morecambe Bay (Leven) and Roose Beck | n/a | Commissioned in 2017 - full year data expected | 1.93 | 6 | 100%
United Utilities | NEWBOLD STREET CSO | Newbold Street CSO | NPSWQD008814 | ROC0057 | SO | CSO on Sewer Network | SD9148013350 | GB112069064720 | Roch (Source to Spodden) | THE STANNEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 29.88 | 42 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEWBRIDGE LANE CSO | Newbridge Lane CSO | 016982657 | STK0087 | SO | CSO on Sewer Network | SJ9039090710 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | 52.93 | 7 | 100%
United Utilities | NEWBRIDGE LANE CSO | Newbridge Lane CSO | 016982656 | STK0086 | SO | CSO on Sewer Network | SJ9039090710 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | NEWBRIDGE LN CROMER ST CSO 432HT | Newby East PS | 016982658 | CAR0084 | SO | Storm Discharge at Pumping Station | SJ9046090780 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Commissioned in 2018 - full year data expected | 166.09 | 69 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEWBRIDGE LN CROMER ST CSO 432HT | Newbridge Lane / Cromer Street CSO | 016982658 | STK0088 | SO | CSO on Sewer Network | SJ9046090780 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | n/a | n/a | Commissioned in 2018 - full year data expected | 0.13 | 1 | 100%
United Utilities | NEWCASTLE ROAD CSO | NEWCASTLE ROAD CSO | 01NEW0006 | NEW0006 | SO | CSO on Sewer Network | SJ7816045520 | GB112068055230 | Checkley Brook - Upper | HAZELEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 365.37 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | NEWCHURCH ROAD BACUP CSO | NEWCHURCH ROAD (Bacup) CSO | 01ROS0033 | ROS0033 | SO | CSO on Sewer Network | SD8625021820 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 3.97 | 10 | 100%
United Utilities | NEWCHURCH ROAD CSO (36013) | Newchurch Road CSO | NPSWQD006555 | ROS0082 | SO | CSO on Sewer Network | SD8461021740 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2020 - full year data expected | 509.24 | 49 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEWCHURCH ROAD/BROOKS STREET CSO | NEWCHURCH ROAD / BROOKS STREET CSO | 01ROS0032 | ROS0032 | SO | CSO on Sewer Network | SD8593021780 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 590.37 | 104 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | NEWCHURCH ROAD/WESLEY PLACE CSO | NEWCHURCH ROAD / WESLEY PLACE CSO | 01ROS0013 | ROS0013 | SO | CSO on Sewer Network | SD8650022060 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 89.8 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEWEARTH ROAD CSO | Newearth Road CSO | 01SAL0061 | SAL0061 | SO | CSO on Sewer Network | SD7267001650 | GB112069061090 | Shaw Brook | TRIBUTARY OF ELLEN BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | NEWLANDS ROAD CSO | Newlands Road CSO | 016983326 | WIG0230 | SO | CSO on Sewer Network | SJ6573099180 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.87 | 6 | 100%
United Utilities | NEWMARKET RD PS | Newmarket Road PS | 01TAM0054 | TAM0054 | SO | Storm Discharge at Pumping Station | SD9250000450 | GB112069061151 | Medlock (Source to Lumb Brook) | TAUNTON BROOK, TRIB OF MEDLOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 98.18 | 33 | 31.78% | Sensor failure / issue | Resolved - December
United Utilities | NEWSHAW LANE CSO | Newshaw Lane CSO | 016982639 | PEA0083 | SO | CSO on Sewer Network | SK0162095230 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | TRIB GLOSSOP BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 33.2 | 34 | 100%
United Utilities | NEWTON ARLOSH WEST PUMPING STATION | Newton Arlosh West PS | 017580259 | ALL0108 | SO | Storm Discharge at Pumping Station | NY1942054480 | 90 | #N/A | TRIBUTARY OF RIVER WAMPOOL | SOLWAY | Silloth | Commissioned in 2018 - full year data expected | 10.13 | 9 | 99.73%
United Utilities | NEWTON ARLOSH WWTW NEWTA | NEWTON ARLOSH WwTW | 017570196 | 17570196 | SO | Inlet CSO at WwTW | NY1909055590 | GB530207614700 | SOLWAY | TRIB OF RIVER WAMPOOL | N/A | N/A | Commissioned in 2018 - full year data expected | 493.4 | 81 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NEWTON REIGNY PUMPING STATION | Newton Reigny PS | NPSWQD002805 | EDE0115 | SO | Storm Discharge at Pumping Station | NY4791031890 | GB102076073992 | Petteril u/s M6 | RIVER PETTERIL | N/A | N/A | Commissioned in 2020 - full year data expected | 238.14 | 33 | 100% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | NEWTOWN PUMPING STATION | Newtown PS | 016983017 | VRY0132 | SO | Storm Discharge at Pumping Station | SJ5258079030 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | n/a | n/a | Commissioned in 2018 - full year data expected | 152.76 | 23 | 99.99%
United Utilities | NO 76 MIDDLE BROOK CSO | No 76 Middle Brook CSO | 01BOL0039 | BOL0039 | SO | CSO on Sewer Network | SD6948008640 | GB112069064540 | Middle Brook | MIDDLE BROOK | North Wirral East | N/A | Commissioned in 2017 - full year data expected | 436.03 | 105 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NOCTORUM AVENUE CSO 512IB | Noctorum Avenue CSO | 016892430 | WIR0072 | SO | CSO on Sewer Network | SJ2807087940 | GB112068060530 | The Birket including Arrowe Brook and Fender | THE RIVER FENDER | n/a | n/a | Commissioned in 2017 - full year data expected | 285.37 | 99 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NORBECK PARK A CSO (SITE 023A9) | Norbeck Park A CSO | 017480286 | COP0083 | SO | CSO on Sewer Network | NY0114015370 | GB112074070000 | Keekle (lower) | NORBECK | n/a | Seascale | Commissioned in 2017 - full year data expected | 68.27 | 63 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | NORDEN/BAMFORD OUTFALL SEWER | Norden/Bamford Outfall SSO | 01ROC0159 | ROC0159 | SO | CSO on Sewer Network | SD8762012590 | GB112069064600 | Roch (Spodden to Irwell) | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023 |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | NORTH ROAD COMBINED SEWER OVERFLOW | NORTH ROAD CSO | 01ALL0011 | ALL0011 | SO | CSO on Sewer Network | NY1504042270 | GB112075073660 | Crookhurst Beck | UNNAMED TRIB OF SANDWITH BECK | N/A | N/A | Commissioned in 2018 - full year data expected | 6.73 | 16 | 99.04%
United Utilities | NORTH ROAD CSO (212IL) | North Road CSO | 016982640 | PEA0084 | SO | CSO on Sewer Network | SK0309094530 | GB112075073660 | Crookhurst Beck | UNNAMED TRIB OF SANDWITH BECK | N/A | N/A | Commissioned in 2018 - full year data expected | 192.13 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NORTH WEST OF HENTHORN ROAD BRIDGE | North West of Henthorn Road Bridge (EO for Lower Moor PS) | 017160099 | RIB0027 | SO | Storm Discharge at Pumping Station | SD7270040600 | GB112071065510 | Mearley Brook | PENDLETON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 362.23 | 49 | 98.1% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NORTH WIRRAL WWTW | North Wirral WwTW (Meols) | 016993400 | 16993400 | SO | Inlet CSO at WwTW | SJ2415090250 | GB112068060530 | The Birket including Arrowe Brook and Fender | LIVERPOOL BAY & RIVER BIRKET | Meols, Morton | Meols | Commissioned in 2016 - full year data expected | 1619.87 | 211 | 99.99% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | NORTH WIRRAL WWTW | North Wirral WwTW (Meols) | 016993400 | 16993400 | SO | Inlet CSO at WwTW | SJ2415090250 | GB112068060530 | The Birket including Arrowe Brook and Fender | LIVERPOOL BAY & RIVER BIRKET | Meols, Morton | Meols | Commissioned in 2016 - full year data expected | 155.24 | 32 | 99.94%
United Utilities | NORTHSIDE CSO 021QB | Northside Sewerage System | 017570206 | ALL0090 | SO | CSO on Sewer Network | NY0117029340 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 180.23 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NORTHUMBERLAND RD/STRETFORD RD CSO | Northumberland Street/Stretford Road CSO | 016982992 | MAN0388 | SO | CSO on Sewer Network | SJ8170096650 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 1733.2 | 289 | 83.54% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NORTHWICH WWTW | NORTHWICH WwTW | 016810099 | 16810099 | ST | Storm Tank at WwTW | SJ6374074160 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | NORTHWICH WWTW | NORTHWICH WwTW | 016810099 | 16810099 | SO | Inlet CSO at WwTW | SJ6374074160 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 4.51 | 7 | 100%
United Utilities | NOTRE DAME GARDENS CSO | NOTRE DAME GARDENS CSO | 01BBN0066 | BBN0066 | SO | CSO on Sewer Network | SD6910028990 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0.23 | 2 | 100%
United Utilities | NR FIRE STN ORMSKIRK RD | Ormskirk Road , Skelmersdale | 017081270 | WLN0049 | SO | CSO on Sewer Network | SD4875005890 | GB112070064790 | Tawd | RIVER TAWD | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | NR FOOTBRIDGE OVER BRK | Monmouth Crescent | 01WIG0119 | WIG0119 | SO | CSO on Sewer Network | SJ5862698924 | GB112069061220 | Millingford (Newton) Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | NR HARRISONS FARM | Near Harrison's Farm CSO | 01CHR0021 | CHR0021 | SO | CSO on Sewer Network | SD5987012400 | GB112070064850 | Douglas - Upper | RIVER DOUGLAS | N/A | N/A | Commissioned in 2020 - full year data expected | 980.81 | 146 | 88.94% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | NUTTALL HALL ROAD CSO | Nuttall Hall Road CSO | 016951212 | BRY0002 | SO | CSO on Sewer Network | SD7958015630 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2016 - full year data expected | 497.27 | 99 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | NW JCT WOODHOUSE LANE | NW Junction Woodhouse Lane CSO | 017091491 | WIG0165 | SO | CSO on Sewer Network | SD5622006750 | GB112070064820 | Douglas - Lower | THE RIVER DOUGLAS | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | O/S 107 LIVERPOOL ROAD CSO 382D3 | O/S 107 Liverpool Road in Footpath CSO | 016982753 | SEF0100 | SO | CSO on Sewer Network | SJ3050098902 | 348 | #N/A | RIVER MERSEY ESTUARY | North Wirral | n/a | Commissioned in 2017 - full year data expected | 35.23 | 28 | 100%
United Utilities | O/S 173 MIDDLEWICH RD | 197 Middlewich Road CSO | 01VRY0092 | VRY0092 | SO | CSO on Sewer Network | SJ6753073601 | GB112068060370 | Wade Brook | WADE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.13 | 3 | 100%
United Utilities | O/S 49 EDWARD ST | Edward Street (Northwich) CSO | 01VRY0093 | VRY0093 | SO | CSO on Sewer Network | SJ6753073602 | GB112068060370 | Wade Brook | WADE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 3.83 | 5 | 100%
United Utilities | O/S 50 BISPHAM AVE | Outside No. 50 Bispham Avenue | 017081264 | SRI0056 | SO | CSO on Sewer Network | SD5335023700 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | O/S 57 WOODHOUSE LANE CSO | O/S 57 WOODHOUSE LANE CSO | 01STA0016 | STA0016 | SO | CSO on Sewer Network | SJ8877059030 | GB112068055360 | Biddulph Brook | TRIB OF BIDDULPH BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 59.07 | 29 | 80.21% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | O/S 65 DOVER ROAD CSO 381P8 | O/s 65 Dover Road CSO | 01SEF0057 | SEF0057 | SO | CSO on Sewer Network | SD3302013220 | GB112070064830 | Three Pool's Waterway | SANDY BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 2.1 | 6 | 100%
United Utilities | O/S 8 HARDY DRIVE CSO | O/S 8 HARDY DRIVE CSO | 01CHR0018 | CHR0018 | SO | CSO on Sewer Network | SD5732017020 | GB112070064952 | Yarrow DS Big Lodge Water | TRIB RIVER CHOR | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | O/S 90 QUEENSWAY CSO | Outside of 90 Queensway CSO | 01VRY0097 | VRY0097 | SO | CSO on Sewer Network | SJ6553066260 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 13.37 | 18 | 99.76%
United Utilities | O/S51 MOORLAND AVE CSO 382G6 | O/s 51 Moorland Avenue | 016982751 | SEF0098 | SO | CSO on Sewer Network | SJ3050098904 | 348 | #N/A | RIVER MERSEY ESTUARY | North Wirral | n/a | Commissioned in 2017 - full year data expected | 340.13 | 104 | 98.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | OAKCLIFFE ROAD CSO | Oakcliffe Road CSO | 016993527 | ROC0040 | SO | CSO on Sewer Network | SD9159014540 | GB112069064690 | Beal | CULVERTED TRIB OF RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 38.07 | 33 | 100%
United Utilities | OAKENBOTTOM ROAD CSO 072IS | Oakenbottom Road CSO | 016982221 | BOL0021 | SO | CSO on Sewer Network | SD7355009171 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 7.37 | 8 | 100%
United Utilities | OAKENROD COMBINED SEWER OVERFLOW | OAKENROD CSO | 016982276 | ROC0080 | SO | CSO on Sewer Network | SD8879013050 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 841.41 | 99 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | OAKFIELD ST COMBINED SEWER OVERFLOW | Oakfield Street CSO | 016892327 | TRA0031 | SO | CSO on Sewer Network | SJ7744087990 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 69.9 | 47 | 65.19% | Sensor failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OAKHURST AVENUE CSO | OAKHURST AVENUE CSO | 01HYN0040 | HYN0040 | SO | CSO on Sewer Network | SD7716030060 | GB112071065490 | Calder - Pendle Water to conf Ribble | CULVERTEDTRIB. OF CLOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 4.4 | 12 | 100%
United Utilities | OAKMERE PUMPING STATION | Oakmere Pumping Station | EPRMB3297NU | CRE0088 | SO | Storm Discharge at Pumping Station | SJ5683568945 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | FIR BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 389.4 | 32 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | OAKWOOD DRIVE CROFTLANDS CSO | Oakwood Drive (Croftlands) Combined Sewer Overflow | 017380296 | LAK0058 | SO | CSO on Sewer Network | SD2907277209 | GB112073071160 | Dragley Beck | DRAGLEY BECK | Morecambe Bay (Leven) | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 87.6% | Sensor failure / issue | Resolved - March
United Utilities | OFF BRANDLESHOLME RD (MH12) CSO | OFF BRANDLESHOLME RD (MH12) CSO | 01BRY0072 | BRY0072 | SO | CSO on Sewer Network | SD7825013500 | GB112069064610 | Kirklees Brook | KIRKLEES BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 111.53 | 39 | 100%
United Utilities | OFF BRIDGE ST | Off Bridge Street PS | 01CHR0032 | CHR0032 | SO | Storm Discharge at Pumping Station | SD6002021410 | GB112070064911 | Lostock US Farington Weir | KENYON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | OFF CARLTON ROAD CSO | Off Carlton Road CSO | EPRSB3398WP | VRY0079 | SO | CSO on Sewer Network | SJ6626073120 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE | N/A | N/A | Commissioned in 2020 - full year data expected | 189.93 | 82 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OFF FOXHOLES ROAD CSO | Off Foxholes Road CSO | 016993392 | TAM0176 | SO | CSO on Sewer Network | SJ9434094000 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB OF RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 11.37 | 16 | 100%
United Utilities | OFF GIBRALTER LANE CSO | Off Gibralter Lane Haughton Green CSO | 016982692 | TAM0164 | SO | CSO on Sewer Network | SJ9395093780 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 96.53 | 77 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OFF GROVE ROAD CSO 44217 | Off Grove Road CSO | 016993726 | TAM0095 | SO | CSO on Sewer Network | SJ9765899782 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | CLVRT SECT SWINESHAW BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 9.37 | 16 | 100%
United Utilities | OFF HUDDERSFIELD ROAD CSO 442JA | Off Huddersfield Road CSO | 016993725 | TAM0116 | SO | CSO on Sewer Network | SJ9785099480 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | CLVRT SEC UNNAMED TRIB RVRTAME | n/a | n/a | Commissioned in 2018 - full year data expected | 0.17 | 4 | 100%
United Utilities | OFF JACK LANE | Jack Lane CSO | 01VRY0066 | VRY0066 | SO | CSO on Sewer Network | SJ6610069200 | GB112068060470 | Dane (Wheelock to Weaver) | TRIB OF PECKMILL BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 8.03 | 8 | 92.99%
United Utilities | OFF JOHN ST CSO (472JC) | Off John Street CSO | 01VRY0004 | VRY0004 | SO | CSO on Sewer Network | SJ6552066270 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER VIA CULVERT | N/A | N/A | Commissioned in 2020 - full year data expected | 0.1 | 1 | 100%
United Utilities | OFF MANOR ROAD CSO 442JF | Off Manor Road CSO | 016982693 | TAM0165 | SO | CSO on Sewer Network | SJ9415094150 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 4.07 | 14 | 100%
United Utilities | OFF MELLOR BROW | Mellor Brook PS | 01RIB0022 | RIB0022 | SO | Storm Discharge at Pumping Station | SD6415031220 | GB112071065500 | Ribble - conf Calder to tidal | 0 | N/A | N/A | Commissioned in 2020 - full year data expected | 166.53 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | OFF MOSS LANE MADELEY CSO | Moss Lane (Madley) Combined Sewer Overflow | 01NEW0005 | NEW0005 | SO | CSO on Sewer Network | SJ7722044970 | GB112068055200 | Lea | RIVER LEA | N/A | N/A | Commissioned in 2019 - full year data expected | 1080.83 | 112 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OFF RODDY LANE CSO (472O5) | Off Roddy Lane CSO | 01VRY0063 | VRY0063 | SO | CSO on Sewer Network | SJ5676074510 | GB112068060550 | Crowton Brook | TRIB OF CROWTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 277.7 | 78 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OFF SCHOOL LANE CSO (472JI) | Off School Lane CSO | 01VRY0060 | VRY0060 | SO | CSO on Sewer Network | SJ6489071570 | GB112068060460 | Weaver (Marbury Brook to Dane) | WEAVER NAVIGATION | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 36.81% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | OFF ST LAWRENCES ROAD CSO | Off St Lawrence Road CSO | 016982771 | TAM0151 | SO | CSO on Sewer Network | SJ9335095090 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB OF RIVER TAME VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 1.27 | 4 | 100%
United Utilities | OFF WALMERSLEY ROAD CSO 092JL | Off Walmersley Road CSO | 016993850 | BRY0134 | SO | CSO on Sewer Network | SD8062013230 | GB112069064620 | Irwell (Rossendale STW to Roch) | PIGS LEA BROOK TRIB RVR IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.98%
United Utilities | OFF WELL LANE KINGSLEY CSO (472JN) | Off Well Lane Kingsley CSO | 01VRY0064 | VRY0064 | SO | CSO on Sewer Network | SJ5528074740 | GB112068060550 | Crowton Brook | KINGSLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.8 | 6 | 100%
United Utilities | OFLOW 6000 WHALEY BRIDGE CSO 211EA | Overflow 6000 at Whaley Bridge CSO | 01PEA0066 | PEA0066 | SO | CSO on Sewer Network | SK0119081740 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | n/a | n/a | Commissioned in 2017 - full year data expected | 47.4 | 17 | 99.98%
United Utilities | OLD EAGLEY CSO 073DM | Old Eagley CSO | 016983216 | BOL0073 | SO | CSO on Sewer Network | SD7233012830 | GB112069064570 | Eagley Brook | EAGLEY BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 222.73 | 51 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | OLD FOLD ROAD CSO | Old Fold Road CSO | 016983225 | WIG0132 | SO | CSO on Sewer Network | SD6188008070 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.1 | 5 | 100%
United Utilities | OLD ROAD CSO | Old Road CSO | 016982635 | PEA0070 | SO | CSO on Sewer Network | SK0229097370 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | SYKE CULVERT TO RIVER ETHEROW | N/A | N/A | Commissioned in 2019 - full year data expected | 0.37 | 11 | 100%
United Utilities | OLDHAM ROAD CSO 35027 | Oldham Road CSO | 01ROC0093 | ROC0093 | SO | CSO on Sewer Network | SD9060010840 | GB112069064600 | Roch (Spodden to Irwell) | CLVRT SEC OF SUDDEN BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 426.02 | 99 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | ST | Storm Tank at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 6.33 | 6 | 100%
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | SO | Inlet CSO at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | ST | Storm Tank at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | ST | Storm Tank at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | OLLERSHAW LANE WW NTWK PS | Ollershaw Lane PS | 01VRY0099 | VRY0099 | SO | Storm Discharge at Pumping Station | SJ6720075750 | GB112068060390 | Peover Eye | TRIBUTARY OF WITTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.26 | 1 | 99.99%
United Utilities | OLLERTON SEWAGE PUMPING STATION | Ollerton PS | 016910012 | MAC0147 | SO | Storm Discharge at Pumping Station | SJ7806076861 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | TRIB MARTHALL BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 99.19 | 28 | 100%
United Utilities | OPP 182 ROCHDALE ROAD CSO (BRY0141) | Opposite 182 Rochdale Road CSO | EPRJB3894EQ | BRY0141 | SO | CSO on Sewer Network | SD8188310641 | GB112069064600 | Roch (Spodden to Irwell) | CLV TRIB OF RIVER ROCH | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | OPP 255 BUXTON ROAD | Opposite 255 Buxton Road CSO | 016982663 | STK0097 | SO | CSO on Sewer Network | SJ9355085860 | GB112069060950 | Poise Brook | HAZEL GROVE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | OPP 76 BURNLEY ROAD CSO | OPP 76 BURNLEY ROAD CSO | 01BUR0021 | BUR0021 | SO | CSO on Sewer Network | SD7960033720 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | OPP RIVER ST CSO (273BY) | Opp River Street CSO | 01MAC0045 | MAC0045 | SO | CSO on Sewer Network | SJ8476081560 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | OPP WEST VIEW COMBINED SEWER O/FLOW | Opp West View CSO | 01ALL0012 | ALL0012 | SO | CSO on Sewer Network | NY1752050520 | GB102075073440 | Waver | STANK BECK | SOLWAY | Silloth | Commissioned in 2018 - full year data expected | 117.13 | 18 | 100%
United Utilities | OPPOSITE 53 MOOR LANE CSO 382G6 | Opposite 53 Moor Lane (in roundabout) Combined Sewer Overflow (Site ID 382G6) (SEF0097) | 016982750 | SEF0097 | SO | CSO on Sewer Network | SJ3050098905 | 348 | #N/A | RIVER MERSEY ESTUARY | North Wirral | n/a | Commissioned in 2017 - full year data expected | 452.77 | 123 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | OPPOSITE NO 1 GRANBY ROAD CSO | Opposite No.1 Granby Road CSO | 016982647 | SAL0169 | SO | CSO on Sewer Network | SD7630000880 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB SINDSLEY BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 42.2 | 69 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OPPOSITE NO 7 CROMER ROAD CSO | Opposite No.7 Cromer Road CSO | 01SEF0056 | SEF0056 | SO | CSO on Sewer Network | SD3302013222 | GB112070064830 | Three Pool's Waterway | TRIB SANDY BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 1.53 | 6 | 100%
United Utilities | OPPOSITE NO. 320 LIVERPOOL ROAD CSO | Opposite No.320 Liverpool Road CSO | 01SEF0053 | SEF0053 | SO | CSO on Sewer Network | SD3319013610 | GB112070064830 | Three Pool's Waterway | SANDY BROOK (TRIB. RIVER ALT) | Ribble | Ainsdale | Commissioned in 2016 - full year data expected | 2.53 | 4 | 100%
United Utilities | OPPOSITE NO.36 CARR LANE CSO | Opposite 36 Carr Lane CSO | 01SEF0054 | SEF0054 | SO | CSO on Sewer Network | SD3302013221 | GB112070064830 | Three Pool's Waterway | SANDY BROOK (TRIB. RIVER ALT) | Ribble | Ainsdale | Commissioned in 2016 - full year data expected | 15.6 | 12 | 98.53%
United Utilities | ORFORD PARK CSO 48087 | Orford Park CSO | NPSWQD010762 | WAR0014 | SO | Storm Discharge at Pumping Station | SJ6113789997 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 619.73 | 75 | 99.66% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ORLANDO STREET CSO 078J3 | Orlando Street CSO | 01BOL0124 | BOL0124 | SO | CSO on Sewer Network | SD7236008520 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Commissioned in 2018 - full year data expected | 30.5 | 26 | 100%
United Utilities | ORMSKIRK ROAD/FRANCE STREET CSO | ORMSKIRK ROAD / FRANCE STREET CSO | 01WIG0008 | WIG0008 | SO | CSO on Sewer Network | SD5710005181 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.3 | 2 | 100%
United Utilities | ORRELL HOUSE FARM CSO 50085 | Orrell House Farm CSO | 017091503 | WIG0173 | SO | CSO on Sewer Network | SD5319006670 | GB112070064820 | Douglas - Lower | DEAN BROOK TRID OF R DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 430.07 | 86 | 99.78% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ORTON STW | ORTON WwTW | 017270008 | 17270008 | ST | Storm Tank at WwTW | NY6291007680 | GB112072071800 | Chapel Beck | CHAPEL BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 2416.72 | 131 | 99.92% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | ORTON STW | ORTON WwTW | 017270008 | 17270008 | SO | Inlet CSO at WwTW | NY6291007680 | GB112072071800 | Chapel Beck | CHAPEL BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 1171.19 | 104 | 99.92% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | OS 49 ST ANDREWS ROAD CSO 38028 | Outside 49 St Andrews Road CSO | 016982650 | SEF0095 | SO | CSO on Sewer Network | SD3079901011 | 172 | #N/A | RIVER MERSEY ESTUARY | North Wirral | n/a | Commissioned in 2018 - full year data expected | 534.9 | 76 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | OSWALDTWISTLE CSO | Oswaldwistle CSO | 017160125 | HYN0008 | SO | CSO on Sewer Network | SD7366028508 | GB112071065050 | Hyndburn Brook - Upper | WHITE ASH BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 282.6 | 62 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OTTERSPOOL ROAD CSO | Otterspool Road Combined Sewer Overflow | 016993555 | STK0005 | SO | CSO on Sewer Network | SJ9365089600 | GB112069061000 | Goyt (Etherow to Mersey) | THE RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | 1325.65 | 153 | 74.16% | Sensor failure / issue | Resolved - December | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OUGHTERBY PUMPING STATION | Oughterby Pumping Station (Site ID 02587) (ALL0067) | 01ALL0067 | ALL0067 | SO | Storm Discharge at Pumping Station | NY2921055660 | 89 | #N/A | UNNAMED TRIB. OF GRASS DYKE | N/A | N/A | Commissioned in 2017 - full year data expected | 50.26 | 5 | 100%
United Utilities | OUGHTRIGHTON LANE CSO 482KO | Oughtrington Lane CSO | 016982896 | WAR0115 | SO | CSO on Sewer Network | SJ6969087430 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | BRIDGEWATER CANAL | n/a | n/a | Commissioned in 2017 - full year data expected | 5.53 | 6 | 100%
United Utilities | OUTS119 RUFFORD RD CSO 382PZ | Outside 1 Teversham | 017081260 | WLN0050 | SO | CSO on Sewer Network | SD3765019790 | GB112070064830 | Three Pool's Waterway | THREE POOLS WATERWAY | N/A | N/A | Commissioned in 2017 - full year data expected | 59.37 | 40 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OUTS119 RUFFORD RD CSO 382PZ | O/S 119 Rufford Road CSO | 017081260 | SEF0092 | SO | CSO on Sewer Network | SD3765019790 | GB112070064830 | Three Pool's Waterway | THREE POOLS WATERWAY | Ribble | Southport | Commissioned in 2017 - full year data expected | 182.67 | 36 | 100%
United Utilities | OUTSIDE 16 CORONATION RD CSO 381PQ | O/S 16 Coronation Road | 016982754 | SEF0101 | SO | CSO on Sewer Network | SJ3050098903 | 348 | #N/A | RIVER MERSEY ESTUARY | North Wirral | n/a | Commissioned in 2017 - full year data expected | 3.57 | 11 | 100%
United Utilities | OUTSIDE 51 CHURCH STREET CSO 471JC | Outside 51 Church Street (Davenham) CSO | 016892455 | VRY0056 | SO | CSO on Sewer Network | SJ6644171121 | GB112068060470 | Dane (Wheelock to Weaver) | ELDERSBRIAR BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1351.93 | 155 | 96.15% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - December
United Utilities | OUTSIDE 81 WODLANE CSO 513OI | Outside 81 Wood Lane CSO | 01WIR0084 | WIR0084 | SO | CSO on Sewer Network | SJ2580088260 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 10.07 | 28 | 99.52%
United Utilities | OUTSIDE 91 STYAL ROAD CSO | Outside 91 Styal Road CSO | 01STK0048 | STK0048 | SO | CSO on Sewer Network | SJ8397087670 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | GATLEY BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 142.47 | 46 | 99.73% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OVER KELLET WWTW | OVER KELLET WwTW | 017370075 | 17370075 | ST | Storm Tank at WwTW | SD5164070240 | GB112073064430 | Keer - Lower | TRIB RIVER KEER | MORECAMBE BAY EAST | N/A | Commissioned in 2018 - full year data expected | 2036.05 | 121 | 100% |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue
United Utilities | OVERTON GARDEN TERRACE PS | Garden Terrace Pumping Station (Site ID GARDE) (LAN0098) | 01LAN0098 | LAN0098 | SO | Storm Discharge at Pumping Station | SD4234058510 | 343 | #N/A | TRIB RIVER LUNE | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | OVERTON PEDDAR-FAR PS | Overton Peddar Far PS | 017280291 | LAN0101 | SO | Storm Discharge at Pumping Station | SD4328057900 | GB112072065950 | Overton Dyke | LADES POOL, TRIB RIVER LUNE | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | OWEN ROAD COMBINED SEWER OVERFLOW | Owen Road CSO | 017280424 | LAN0116 | SO | CSO on Sewer Network | SD4788062360 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 36.7 | 5 | 99.98%
United Utilities | OWLEY WOOD ROAD CSO | OWLEY WOOD ROAD CSO | 01VRY0083 | VRY0083 | SO | CSO on Sewer Network | SJ6255074270 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Commissioned in 2018 - full year data expected | 103.9 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | OXCLIFFE RD PS NO 1 & EO TO OVERTON | Oxcliffe Road Pumping Station (Site ID 25006) (LAN0028) | 01LAN0028 | LAN0028 | SO | Storm Discharge at Pumping Station | SD4476061080 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 0 | 0 | 99.93%
United Utilities | OXFORD RD/HOLLINS ROAD CSO | Oxford Road/Hollins Road CSO | 017190824 | PEN0004 | SO | CSO on Sewer Network | SD8731038750 | GB112071065150 | Colne Water - Wanless Water to Pendle Water | SWINDEN CLOUGH | N/A | N/A | Commissioned in 2020 - full year data expected | 1.03 | 7 | 100%
United Utilities | OXFORD ROAD/GROSVENOR STREET CSO | OXFORD ROAD / GROSVENOR STREET CSO | 01MAN0189 | MAN0189 | SO | CSO on Sewer Network | SJ8415097461 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 81.33 | 26 | 98.23%
United Utilities | OXFORD STREET/AINSLIE STREET CSO | Oxford Street/Ainsley Street CSO | 017480304 | BRW0091 | SO | CSO on Sewer Network | SD1966070553 | 344 | #N/A | ORMSGILL RESERVOIR | WALNEY EAST | Walney West Shore | Commissioned in 2016 - full year data expected | 56.17 | 28 | 92.5%
United Utilities | PADDINGTON PS 48028 | Paddington PS | 01WAR0030 | WAR0030 | SO | Storm Discharge at Pumping Station | SJ6381088930 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PALACE NOOK SEWAGE PUMPING STATION | Palace Nook Sewage Pumping Station (Site ID04522) (BRW0097) | 017480314 | BRW0097 | SO | Storm Discharge at Pumping Station | SD1887071800 | GB641211172000 | Duddon Sands | WALNEY CHANNEL | Duddon and Walney | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 452.64 | 55 | 98.23% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | PALMERSTON ST SHRIGLEY RD 272KZ | Palmerston Street/Shrigley Road CSO | 01MAC0121 | MAC0121 | SO | CSO on Sewer Network | SJ9395077990 | GB112069060660 | Harrop Brook | HARROP BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 203 | 210 | 99.46% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PALMERSTON ST SHRIGLEY RD 272KZ | Palmerston Street CSO | 01MAC0121 | MAN0402 | SO | CSO on Sewer Network | SJ9395077990 | GB112069060660 | Harrop Brook | HARROP BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | PALMERSTON STREET CSO | Palmerston Street CSO | 016983280 | MAN0401 | SO | CSO on Sewer Network | SJ8589097990 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.13 | 3 | 100%
United Utilities | PAPCASTLE PUMPING STATION (ALL0139) | Papcastle Pumping Station | EPRJB3597VV | ALL0139 | SO | Storm Discharge at Pumping Station | NY1035931293 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Commissioned in 2020 - full year data expected | 4.34 | 4 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | PARDSHAW STW | PARDSHAW WwTW | 017570049 | 17570049 | ST | Storm Tank at WwTW | NY0990024680 | GB112075070540 | Marron | BLACK BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 214.93 | 53 | 98.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PARK HALL FARM CSO 071EY | PARK HALL FARM CSO | 01BOL0143 | BOL0143 | SO | CSO on Sewer Network | SD6271009630 | GB112069064540 | Middle Brook | UNNAMED TRIB OF MIDDLE BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 151.6 | 65 | 95.44% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | PARK LANE CSO 50098 | Park Lane CSO | 016993708 | WIG0082 | SO | CSO on Sewer Network | SJ6725099700 | GB112069060810 | Bedford Brook | BEDFORD BROOK TRIB GLAZE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 1077.82 | 78 | 95.41% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PARK LANE D/S OF S.W. | Park Lane PS | 01BRY0075 | BRY0075 | SO | Storm Discharge at Pumping Station | SD7998004962 | GB112069061451 | Irwell (Croal to Irk) | UNKNOWN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PARK ROAD (STRETFORD) CSO | Birch Road CSO | EPRSB3398EX | TRA0046 | SO | CSO on Sewer Network | SJ7088091510 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 289.6 | 107 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PARK ROAD (STRETFORD) CSO | Park Road (Stretford) CSO | EPRSB3398RR | TRA0047 | SO | CSO on Sewer Network | SJ7088091510 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | BENT LANE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.27 | 3 | 100%
United Utilities | PARK ROAD ARTHOG ROAD CSO 452LS | Park Road/Arthog Road CSO | 01TRA0078 | TRA0078 | SO | CSO on Sewer Network | SJ7752085720 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | n/a | n/a | Commissioned in 2018 - full year data expected | 763.9 | 144 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PARK ROAD COMBINED SEWER OVERFLOW | Park Road CSO | 01BUR0013 | BUR0013 | SO | CSO on Sewer Network | SD8637030180 | GB112071065060 | Calder - headwaters to conf Brun | RIVER CALDER | N/A | N/A | Commissioned in 2017 - full year data expected | 0.33 | 1 | 100%
United Utilities | PARK ROAD NORTH | Park Road North | 01STH0076 | STH0076 | SO | CSO on Sewer Network | SJ5913095410 | GB112069061220 | Millingford (Newton) Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PARK ST/SWINTON HALL ROAD CSO | Park Street/Swinton Hall Road | EPRTB3192VK | SAL0101 | SO | CSO on Sewer Network | SD7804001100 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB FOLLY BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 6.7 | 26 | 100%
United Utilities | PARK STREET COMBINED SEWER OVERFLOW | Park Street SO | 016930977 | LIV0028 | SO | CSO on Sewer Network | SJ3470088000 | 167 | #N/A | RIVER MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | PARKGATE FARM (WARBURTON) CSO | Parkgate Farm Warburton CSO | EPRSB3398VQ | TRA0050 | SO | CSO on Sewer Network | SJ6989089800 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 225.17 | 52 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PARKLANDS CSO 123JR CHR0015 | Parklands CSO | 017081354 | CHR0015 | SO | CSO on Sewer Network | SD5694017740 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER CHOR TRIB RIVER YARROW | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | PARR BRIDGE/MOSLEY COMMON RD CSO | Parr Bridge/Mosley Common Road CSO | 016982787 | WIG0209 | SO | CSO on Sewer Network | SD7137001500 | GB112069061100 | Astley Brook (Mersey) | HONKSFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 41.87 | 30 | 100%
United Utilities | PARR BROOK CSO | PARR BROOK CSO | 016983249 | BRY0133 | SO | CSO on Sewer Network | SD8157007270 | GB112069064600 | Roch (Spodden to Irwell) | PARR BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 86.3 | 35 | 100%
United Utilities | PARROTT STREET/BROMLOW STREET CSO | PARROT STREET / BROMLOW STREET CSO | 01MAN0107 | MAN0107 | SO | CSO on Sewer Network | SJ8779097891 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CORN BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 24.5 | 20 | 99.99%
United Utilities | PARTINGTON WWTW | PARTINGTON WwTW | 016940148 | 16940148 | ST | Storm Tank at WwTW | SJ7052090860 | GB112069060980 | Sinderland Brook | RED BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 392.82 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PARTON N.F. SHORE PUMPING STATION | Parton PS | 017470154 | COP0048 | SO | Storm Discharge at Pumping Station | NX9773020230 | 356 | #N/A | IRISH SEA | n/a | n/a | Commissioned in 2018 - full year data expected | 35.66 | 102 | 98.66% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PEEL HALL CSO (BRY0140) | Peel Hall Drive CSO | EPRJB3895AY | BRY0140 | SO | CSO on Sewer Network | SD7890014654 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PEEL HALL DRIVE CSO | Peel Hall Drive CSO | 01BRY0004 | BRY0004 | SO | CSO on Sewer Network | SD7898014680 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2016 - full year data expected | 129.47 | 69 | 98.75% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | PEEL LANE CSO NO. 1 | Peel Lane CSO No 1 STORM OVERFLOW | 016993593 | ROC0119 | SO | CSO on Sewer Network | SD8474011330 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 137.94 | 64 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PEEL LANE NO 2 CSO | Peel Lane No. 2 CSO | 01ROC0165 | ROC0165 | SO | CSO on Sewer Network | SD8485011210 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 110.41 | 63 | 99.89% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PENKFORD BRIDGE | Penkford Bridge | 01STH0110 | STH0110 | SO | CSO on Sewer Network | SJ5622094900 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | 0 | N/A | N/A | Commissioned in 2019 - full year data expected | 13.5 | 29 | 100%
United Utilities | PENN LANE WESTON POINT PR CSO 202LE | Penn Lane (Weston Point, Point R) combined sewer overflow (202LE) (HAL0060) | 01HAL0060 | HAL0060 | SO | CSO on Sewer Network | SJ4977082451 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 95.9 | 68 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PENNINGTON LANE CSO | Pennington Lane CSO | EPRSB3399EK | WAR0008 | SO | CSO on Sewer Network | SJ5556893645 | GB112069061170 | Sutton Brook | SANKEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 951.43 | 149 | 100% |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue
United Utilities | PENNINGTON MILL BRIDGE CSO | Pennington Mill bridge CSO | 01WIG0143 | WIG0143 | SO | CSO on Sewer Network | SJ6541099210 | GB112069060760 | Pennington Brook (Glaze) | 0 | N/A | N/A | Commissioned in 2019 - full year data expected | 9.2 | 14 | 100%
United Utilities | PENNY BRIDGE CSO | Penny Bridge CSO | 017190752 | CRA0002 | SO | CSO on Sewer Network | SD8145063271 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | RIVER RIBBLE | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | PENNY LANE GRIMESBOTTOM CSO 43122 | Penny Lane (Grimesbottom) CSO | 016982654 | STK0081 | SO | CSO on Sewer Network | SJ8975091240 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 229.6 | 52 | 99.81% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | PENRITH GRAMMAR SCHOOL | Calthwaite Ww Pumping Station (CALPumping Station) (EDE0036) | 01EDE0036 | EDE0036 | SO | Storm Discharge at Pumping Station | NY5188029730 | GB102076071020 | Eamont (Upper) | DOG BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 16.65 | 10 | 100%
United Utilities | PENRITH OUTFALL CSO | Penrith Outfall CSO | 017680281 | EDE0081 | SO | CSO on Sewer Network | NY5417029470 | GB102076070990 | Eamont (Lower) | RIVER EAMONT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PENRITH RD | Penrith Road | 01ALL0070 | ALL0070 | SO | CSO on Sewer Network | NY2724023660 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER GRETA | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PENRITH SPS | Gillwilly PS | 017670039 | EDE0119 | SO | Storm Discharge at Pumping Station | NY5082030500 | GB102076071020 | Eamont (Upper) | THACKA BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PENRITH WWTW (PENRT) | PENRITH WwTW | 017670084 | 17670084 | ST | Storm Tank at WwTW | NY5525029570 | GB102076070990 | Eamont (Lower) | RIVER EAMONT | N/A | N/A | Commissioned in 2019 - full year data expected | 443.52 | 30 | 100%
United Utilities | PENRUDDOCK SPS | Penruddock Sewage PS | 017680293 | EDE0094 | SO | Storm Discharge at Pumping Station | NY4293028190 | GB102076073992 | Petteril u/s M6 | TRIB RIVER PETTERIL | N/A | N/A | Commissioned in 2020 - full year data expected | 51.44 | 37 | 99.99%
United Utilities | PEPPERMINT BRIDGE CSO | Peppermint Bridge CSO | EPRJB3896EL | ROC0192 | SO | CSO on Sewer Network | SD9437211958 | GB112069064690 | Beal | PIETHORNE BROOK TRIB RVR BEAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PERCY STREET CSO | Percy Street CSO | 017190768 | PRE0003 | SO | CSO on Sewer Network | SD5528128742 | 176 | #N/A | STORM CULVERT,TRIB OF RIBBLE | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PETER STREET CSO 212LL | Peter Street Combined Sewer Overflow (212LL) (PEA0082) | 016982638 | PEA0082 | SO | CSO on Sewer Network | SK0207096970 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | n/a | n/a | Commissioned in 2018 - full year data expected | 0.3 | 4 | 99.91%
United Utilities | PETRE ARMS ROUNDABOUT CSO | Petre Arms Roundabout CSO | 01RIB0017 | RIB0017 | SO | CSO on Sewer Network | SD7090034837 | GB112071065490 | Calder - Pendle Water to conf Ribble | STREAM TRIB BUSHBURN BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | PETTERIL RAILWAY BRIDGE SSO | D/S Petterill Railway Bridge | 017670038 | CAR0030 | SO | CSO on Sewer Network | NY4138055060 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Commissioned in 2020 - full year data expected | 32.17 | 5 | 91.41%
United Utilities | PHILIPS DRIVE (WHITEFIELD) CSO | Phillips Drive (Whitefield) CSO | 016951196 | BRY0127 | SO | CSO on Sewer Network | SD7998004961 | GB112069061451 | Irwell (Croal to Irk) | TRIB BRADLEY BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 367.99 | 70 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PHILIPS ROAD CSO | Philips Road CSO | EPRWP3723KF | BBN0167 | SO | CSO on Sewer Network | SD6952129023 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | PHILIPS ROAD CSO (052LO) | PHILLIPS ROAD CSO | 01BBN0060 | BBN0060 | SO | CSO on Sewer Network | SD6979029590 | GB112071065310 | Blakewater | TRIB OF RIVER BLAKEWATER V SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 519.07 | 117 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | PICA STW | PICA WwTW | 017470038 | 17470038 | ST | Storm Tank at WwTW | NY0232022860 | GB112074070040 | Lowca Beck | DYAN BECK | N/A | N/A | November 2021 | 300.03 | 70 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PICKET HOW FARM SSO | Pickett How Farm CSO | 017470089 | COP0062 | SO | CSO on Sewer Network | NY0117009690 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Commissioned in 2016 - full year data expected | 118.94 | 13 | 84.5% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | PILLING LANE PS | Pilling Lane Pumping Station (Site ID PILLL) (WYR0073) | 017290557 | WYR0073 | SO | Storm Discharge at Pumping Station | SD3607048950 | GB641211171000 | Morecambe Bay | RIVER WYRE ESTUARY | Morecambe Bay East, Lune (Wyre Estuary) and Lune (Broadfleet and Plover Scar) | Fleetwood and Morecambe South | Commissioned in 2017 - full year data expected | 1.65 | 17 | 100%
United Utilities | PIMHOLE CSO | Pimhole CSO | 01BRY0021 | BRY0021 | SO | CSO on Sewer Network | SD8147010180 | GB112069064600 | Roch (Spodden to Irwell) | BARN BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 44.47 | 40 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PLATT LANE COMBINED SEWER OVERFLOW | PLATT LANE CSO | 016941067 | WIG0016 | SO | CSO on Sewer Network | SJ8490094400 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | PLATT BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 3 | 5 | 100%
United Utilities | PLATT LANE COMBINED SEWER OVERFLOW | Platt Lane CSO | 016941067 | MAN0017 | SO | CSO on Sewer Network | SJ8490094400 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | PLATT BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 1.37 | 1 | 100%
United Utilities | PLAYFAIR ST | Playfair St/Park Row CSO | 01BOL0069 | BOL0069 | SO | CSO on Sewer Network | SD7175012950 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PLUMBLAND WWTW | Plumbland WwTW | 017570072 | 17570072 | ST | Storm Tank at WwTW | NY1394040300 | GB112075073640 | Ellen (lower) | RIVER ELLEN | n/a | n/a | Commissioned in 2018 - full year data expected | 5033.48 | 253 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | PLUMLEY STW | PLUMLEY WwTW | 016810103 | 16810103 | SO | Inlet CSO at WwTW | SJ7171075190 | GB112068060390 | Peover Eye | PEOVER EYE (VIA TRIB) | N/A | N/A | Commissioned in 2020 - full year data expected | 67.81 | 45 | 99.92% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PLUMPTON NORTH WWTW PLUMN | PLUMPTON NORTH WwTW | 017670110 | 17670110 | SO | Inlet CSO at WwTW | NY4910037520 | GB102076073991 | Petteril d/s M6 | RIVER PETTERIL | n/a | n/a | Commissioned in 2018 - full year data expected | 186.29 | 29 | 99.99%
United Utilities | POOL BANK FARM BOWDON CSO 452L6 | Pool Bank Farm, Bowdon CSO | 01TRA0053 | TRA0053 | SO | CSO on Sewer Network | SJ7495085601 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | n/a | n/a | Commissioned in 2018 - full year data expected | 424.97 | 93 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | POOLEY BRIDGE EAST WWTW | Pooley Bridge East wastewater treatment works (Site ID POOLE) (017670085) | 017670085 | 17670085 | SO | Inlet CSO at WwTW | NY4717024720 | GB102076071020 | Eamont (Upper) | RIVER EAMONT | N/A | N/A | Commissioned in 2016 - full year data expected | 5.32 | 4 | 99.96%
United Utilities | POOLEY BRIDGE PUMPING STATION | Pooley Bridge SSO | 017680473 | EDE0060 | SO | CSO on Sewer Network | NY4698024440 | GB102076071020 | Eamont (Upper) | RIVER EAMONT | N/A | N/A | Commissioned in 2016 - full year data expected | 313.13 | 47 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | POOLSTOCK LANE/HOLT STREET CSO | Poolstock Lane/ Holt Street CSO | EPRQP3420GZ | WIG0253 | SO | CSO on Sewer Network | SD5727903869 | GB112070061600 | Smithy Brook | SMITHY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 4.37 | 3 | 100%
United Utilities | POPLAR COTTAGES CSO | Poplar Cottages CSO | 016881722 | VRY0135 | SO | CSO on Sewer Network | SJ6456077200 | GB112068060400 | Forge (Kidd) Brook | TRIB OF KID BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 12.27 | 10 | 100%
United Utilities | PORT CARLISLE PUMPING STATION | Port Carlisle Pumping Station (Site ID PRTCA) (ALL0135) | 017680456 | ALL0135 | SO | Storm Discharge at Pumping Station | NY2412162461 | 90 | #N/A | THE SOLWAY FIRTH | Solway | n/a | Commissioned in 2017 - full year data expected | 4.85 | 5 | 100%
United Utilities | PORT CAUSEWAY/CROSSWAY CSO | Port Causeway/Crossway CSO | 016881733 | WIR0125 | SO | CSO on Sewer Network | SJ3441083751 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | BROMBOROUGH POOL | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 1.43 | 15 | 100%
United Utilities | PORTINSCALE SEWAGE PUMPING STATION | Portinscale SPS | 01ALL0088 | ALL0088 | SO | Storm Discharge at Pumping Station | NY2465023950 | GB112075070440 | Newlands Beck | POW BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 815.96 | 115 | 99.82% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | POTTERS LANE CSO | POTTERS LANE CSO | 01MAN0095 | MAN0095 | SO | CSO on Sewer Network | SD8630001140 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED SECTION MOSTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Capital / maintenance works affect EDM operation | N/A - Ongoing investigation
United Utilities | POTTINGER ST/OXFORD ST | Pottinger Street/Oxford Street CSO | 016993753 | TAM0045 | SO | CSO on Sewer Network | SJ9288097810 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 189.73 | 66 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | POWERHOUSE ROAD PUMPING STATION | Power House Road PS | 016881966 | WIR0044 | SO | Storm Discharge at Pumping Station | SJ3718080570 | 171 | #N/A | MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 211.36 | 50 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | POWIS ROAD CSO 332MG PRE0025 | Powis Road CSO | 017160321 | PRE0025 | SO | CSO on Sewer Network | SD5140229892 | 176 | #N/A | CHAIN CAUL CULVERT | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | POYNTON BALANCING TANK | Field No. 556, Mill Hill, Poynton CSO | 01MAC0051 | MAC0051 | SO | CSO on Sewer Network | SJ9158085330 | GB112069060940 | Micker Brook | NORBURY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1425.48 | 89 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | PREESALL WWTW PREES | PREESALL WwTW | 017260071 | 17260071 | ST | Storm Tank at WwTW | SD3481046870 | GB531207212200 | WYRE | WYRE ESTUARY | Lune (Wyre Estuary) and Lune (Broadfleet and Plover Scar) | Fleetwood | Commissioned in 2017 - full year data expected | 885.2 | 60 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | PRESTON NETWORK TERMINAL PUMPING ST | Preston Network Terminal Pumping Station (Site ID HOWCK) (PRE0125) | EPRMB3990NU | PRE0125 | SO | Storm Discharge at Pumping Station | SD5037729025 | 175 | #N/A | TIDAL RIVER RIBBLE | N/A | N/A | Commissioned in 2017 - full year data expected | 97.82 | 18 | 100%
United Utilities | PRESTON NEW ROAD | Yew Tree Drive CSO | 017091436 | BBN0026 | SO | CSO on Sewer Network | SD6564029540 | GB112071065300 | Darwen - conf Roddlesworth to tidal | TRIB OF ARLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 375.15 | 87 | 97.75% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | PRESTON WASTEWATER TREATMENT WORKS | PRESTON WwTW | 017160064 | 17160064 | ST | Storm Tank at WwTW | SD4571027930 | 176 | #N/A | RIVER RIBBLE ESTUARY | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2017 - full year data expected | 1180.63 | 95 | 99.81% |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation
United Utilities | PRESTWICH CLOUGH CSO 09034 | Prestwich Clough CSO | 016983247 | BRY0040 | SO | CSO on Sewer Network | SD8117003530 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 5.66 | 10 | 99.98%
United Utilities | PRESTWICH GOLF COURSE CSO 093IR | Prestwich Golf Course CSO | 016983241 | BRY0132 | SO | CSO on Sewer Network | SD8150002170 | GB112069061451 | Irwell (Croal to Irk) | SINGLETON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 14.4 | 19 | 100%
United Utilities | PRESTWICH PS | Prestwich PS | 016983172 | BRY0078 | SO | Storm Discharge at Pumping Station | SD7986003070 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 685.43 | 119 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | PRIESTLEY CLOUGH CSO | PRIESTLY CLOUGH CSO | 01HYN0028 | HYN0028 | SO | CSO on Sewer Network | SD7603027270 | GB112071065040 | Hyndburn | WOODNOOK WATER | N/A | N/A | Commissioned in 2019 - full year data expected | 22.8 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | PRIMROSE HILL CSO | Primrose Hill CSO | 01BRY0022 | BRY0022 | SO | CSO on Sewer Network | SD8151010320 | GB112069064600 | Roch (Spodden to Irwell) | BARN BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 156.07 | 104 | 91.62% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | PRIMROSE LANE CSO | Primrose Lane CSO | 016892340 | PEA0029 | SO | CSO on Sewer Network | SK0232094110 | GB112069060700 | Long Clough Brook | LONG CLOUGH BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 141.74 | 60 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | #N/A | Primrose Street/Ellesmere Street CSO | 016983323 | WIG0235 | SO | CSO on Sewer Network | SD6875102302 | GB112069060810 | Bedford Brook | SHAKERLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PRINCES PRKWAY/M60 CSO 28051 | Princess Parkway/M60 CSO | 016942049 | MAN0020 | SO | CSO on Sewer Network | SJ8254191081 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 283.43 | 38 | 100%
United Utilities | PRINCES STREET CSO | Prince's Street CSO | 016982672 | STK0108 | SO | CSO on Sewer Network | SJ8948090590 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2016 - full year data expected | 64 | 45 | 76.99% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery
United Utilities | PRINCESS RD (PETER ST) CSO (50006) | Princess Road (St.Peter) CSO | 016983355 | WIG0037 | SO | CSO on Sewer Network | SJ5861098950 | GB112069061220 | Millingford (Newton) Brook | MILLINGFORD BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 84.14 | 37 | 99.89%
United Utilities | PRINCESS ST/WHITWORTH ST CSO 282MN | Princess Street/Whitworth Street CSO | 016982950 | MAN0354 | SO | CSO on Sewer Network | SJ8433097521 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 19.97 | 21 | 100%
United Utilities | PRINGLE STREET CSO | PRINGLE STREET CSO | 01BBN0054 | BBN0054 | SO | CSO on Sewer Network | SD6939027460 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0.17 | 2 | 100%
United Utilities | PRIORY ROAD CSO 392MO | Priory Road, Ulverston | 01LAK0005 | LAK0005 | SO | Storm Discharge at Pumping Station | SD2973076700 | 181 | #N/A | TRIB CARTER POOL | MORECAMBE BAY (LEVEN) | N/A | Commissioned in 2018 - full year data expected | 62.6 | 22 | 100%
United Utilities | PROMENADE COMBINED SEWER OVERFLOW | Promenade CSO | 017370196 | LAK0072 | SO | CSO on Sewer Network | SD4067077560 | GB531207312000 | KENT | THE KENT CHANNEL MORECAMBE BAY | MORECAMBE BAY EAST | N/A | Commissioned in 2018 - full year data expected | 20.4 | 20 | 100%
United Utilities | PROSPECT AND OUGHTERSIDE WWTW PRSPO | PROSPECT & OUGHTERSIDE WwTW | 017570073 | 17570073 | SO | Inlet CSO at WwTW | NY1170040020 | GB112075073640 | Ellen (lower) | SALTERWATH BECK | Silloth | Allonby | Commissioned in 2017 - full year data expected | 659.75 | 121 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | PS AT BRYN GATES | Bryn Gates PS | 01WIG0117 | WIG0117 | SO | Storm Discharge at Pumping Station | SD5947000900 | GB112069064520 | Hey/Borsdane Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | PUNCH BOWL HOTEL (ASKHAM) CSO | Punch Bowl Hotel (Askham) CSO | 01EDE0008 | EDE0008 | SO | CSO on Sewer Network | NY5159023780 | GB102076071010 | Lowther (Lower) | ASKHAM BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 19.97 | 11 | 88.01% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | QUARRY BANK MILL CSO 272M4 | QUARRY BANK MILL CSO | 01MAC0043 | MAC0043 | SO | CSO on Sewer Network | SJ8344082800 | GB112069061381 | Bollin (River Dean to Ashley Mill) | TRIBUTARY OF RIVER BOLLIN | N/A | N/A | Commissioned in 2018 - full year data expected | 79.7 | 17 | 100%
United Utilities | QUEENS PARK (NO 1) | Queens Park Drive (Crewe) CSO | 01CRE0031 | CRE0031 | SO | CSO on Sewer Network | SJ6856055440 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 79.02 | 29 | 100%
United Utilities | QUEENS PARK NO 2 CSO | Queens Park Golf Club CSO | 01CRE0032 | CRE0032 | SO | CSO on Sewer Network | SJ6850055420 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 19.53 | 11 | 100%
United Utilities | QUEENS PARK ROAD CSO | Queens Park Road CSO | EPRJP3122XY | BBN0016A | SO | CSO on Sewer Network | SD6934827603 | GB112071065310 | Blakewater | QUEENS PARK CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 47.74 | 31 | 99.99%
United Utilities | QUEENS ROAD (DARWEN) CSO | Queen's Road CSO | 017180470 | BBN0145 | SO | CSO on Sewer Network | SD6966020510 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | QUEENS ROAD COMBINED SEWER OVERFLOW | QUEENS ROAD CSO | NPSWQD010957 | MAN0055 | SO | CSO on Sewer Network | SD8575000490 | GB112069061131 | Irk (Wince to Irwell) | MOSS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 21.5 | 31 | 99.99%
United Utilities | QUEENS ROAD/SCORPTON STREET CSO | Queens Road/Hendham Vale CSO | 016982952 | MAN0081 | SO | CSO on Sewer Network | SD8574000500 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED SECTION MOSTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.53 | 13 | 100%
United Utilities | QUEENS ROAD/SCORPTON STREET CSO | Queens Road/Scorpton Street CSO | 016982952 | MAN0351 | SO | CSO on Sewer Network | SD8574000500 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED SECTION MOSTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.93 | 3 | 100%
United Utilities | QUEENSWAY CSO | The Queensway CSO | 016892228 | SAL0193 | SO | CSO on Sewer Network | SD7915001870 | GB112069061451 | Irwell (Croal to Irk) | SLACK BROOK VIA SUFACE WATER S | n/a | n/a | Commissioned in 2018 - full year data expected | 64.88 | 27 | 100%
United Utilities | QUEENSWAY PS | Higher Folds (Queensway) PS | 01WIG0101 | WIG0101 | SO | Storm Discharge at Pumping Station | SD6746000370 | GB112069060810 | Bedford Brook | PEN LEACH BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 392.64 | 24 | 99.99%
United Utilities | RADCLIFFE CENTRAL CSO | OUTSIDE THE BRIDGE TAVERN CSO | 01BRY0030 | BRY0030 | SO | CSO on Sewer Network | SD7860006950 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 218.63 | 81 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RADFORD STREET CSO | Radford Street CSO | 016993605 | SAL0079 | SO | CSO on Sewer Network | SD8212001500 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 30.57 | 40 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RAGLAN STREET CSO 44180 | Raglan Street CSO | 01TAM0020 | TAM0020 | SO | CSO on Sewer Network | SJ9426094740 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 409.74 | 105 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | RAILWAY FARM CSO 25051 | Railway Farm Combined Sewer Overflow (Site ID 25051) (LAN0031) | 017220120 | LAN0031 | SO | CSO on Sewer Network | SD4808055240 | GB112072065900 | Conder | RIVER CONDOR | Lune (Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 103.66 | 30 | 99.99%
United Utilities | RAILWAY ROAD/SOUTH STREET CSO | RAILWAY ROAD / SOUTH STREET CSO | 01BBN0121 | BBN0121 | SO | CSO on Sewer Network | SD6928022300 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | CLVRTD SECTION OF RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | RAILWAY STREET CSO | Railway Street CSO | 01BRY0005 | BRY0005 | SO | CSO on Sewer Network | SD7898014681 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2016 - full year data expected | 0 | 0 | 98.43%
United Utilities | RAINSOUGH BROW CSO | Rainsough Brow CSO | 016983242 | BRY0053 | SO | CSO on Sewer Network | SD8069002040 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 313.38 | 103 | 99.46% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | RAMPARTS CSO 25075 | Ramparts CSO | 017280425 | LAN0072 | SO | CSO on Sewer Network | SD4792062410 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 6.76 | 4 | 99.92%
United Utilities | RAMPSIDE PUMPING STATION | Rampside Village PS | 01BRW0071 | BRW0071 | SO | Storm Discharge at Pumping Station | SD2390065800 | 342 | #N/A | MORECAMBE BAY | Walney and Roose Beck | Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 379.72 | 55 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | RAMSGREAVE DRIVE CSO | Ramsgreave Drive CSO | 017180475 | BBN0150 | SO | CSO on Sewer Network | SD6824030760 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | RASSBOTTOM STREET CSO | Rassbottom Street CSO | 016940471 | TAM0039 | SO | CSO on Sewer Network | SJ9588098580 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 1.17 | 4 | 99.98%
United Utilities | RATING LANE/MEADOWLANDS AVENUE CSO | Rating Lane/Meadowlands Avenue CSO | 01BRW0037 | BRW0037 | SO | CSO on Sewer Network | SD2194069339 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BRIDGE/MILLBECK | Walney and Roose Beck | n/a | Commissioned in 2016 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Site does not discharge to the environment. Permit under review with Environment Agency
United Utilities | RAVENGLASS STW | RAVENGLASS WwTW | 017470074 | 17470074 | SO | Inlet CSO at WwTW | SD0853096020 | 186 | #N/A | RIVER ESK | Ravenglass | N/A | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | RAVENSTONEDALE STW | RAVENSTONEDALE WwTW | 017670024 | 17670024 | SO | Inlet CSO at WwTW | NY7212004600 | GB102076070600 | Scandal Beck | SANDAL BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 2105.54 | 143 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RAVENSTOWN PUMPING STATION | Ravenstown PS | 017380497 | LAK0103 | SO | Storm Discharge at Pumping Station | SD3616074931 | 181 | #N/A | WINDERMOOR MAIN DRAIN | Morecambe Bay (Leven) | n/a | Commissioned in 2017 - full year data expected | 37.84 | 10 | 99.96%
United Utilities | RAVENSWOOD CSO 52568 | Ravenswood Drive CSO | 017290504 | WYR0079 | SO | CSO on Sewer Network | SD3371037610 | 180 | #N/A | HORSEBRIDGE DYKE | Lune (Wyre Estuary) and Lune (Broadfleet and Plover Scar) | Fleetwood | Commissioned in 2017 - full year data expected | 31.38 | 19 | 100%
United Utilities | RAWNSLEY HALL PUMPING STATION | Rawnsley Hall PS (AKA Greta Grove) | 017580420 | ALL0021 | SO | Storm Discharge at Pumping Station | NY2617023680 | GB112075073561 | Derwent US Bassenthwaite Lake | THE RIVER GRETA | n/a | n/a | Commissioned in 2017 - full year data expected | 68.76 | 40 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | REAR 23 LIVERPOOL ROAD NORTH CSO | Rear 23 Liverpool Road North CSO | 016997082 | SEF0015 | SO | CSO on Sewer Network | SD3685002290 | GB112069061441 | Alt US Bull Bridge | MAGHULL BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | REAR 237 RUNCORN ROAD CSO (472PR) | Rear 237 Runcorn Road CSO | 01VRY0051 | VRY0051 | SO | CSO on Sewer Network | SJ6292075180 | GB112068060510 | Cogshall Brook | TRENT AND MERSEY CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 89.6 | 90 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | REAR 24 BISPHAM AVENUE CSO | Rear of No. 24 Bispham Avenue CSO | EPRSB3398AS | SRI0024 | SO | CSO on Sewer Network | SD5343023820 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | REAR GARDEN OF 16 CROSSINGS CLOSE | Rear Garden of No.16 Crossings Close | 017480387 | COP0095 | SO | CSO on Sewer Network | NY0114015360 | GB112074070000 | Keekle (lower) | NOR BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | REAR MEADOW LANE CSO | Rear of 67 Meadow Lane CSO | 01VRY0106 | VRY0106 | SO | CSO on Sewer Network | SJ6611069210 | GB112068060470 | Dane (Wheelock to Weaver) | TRIB PECKMILL BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 3.1 | 2 | 36.81% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | REAR NO.1 HASTINGS ROAD CSO 381P8 | Rear No.1 Hastings Road CSO | 01SEF0055 | SEF0055 | SO | CSO on Sewer Network | SD3302013223 | GB112070064830 | Three Pool's Waterway | SANDY BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 2.03 | 7 | 100%
United Utilities | REAR OF 125 BAKER STREET CSO | Rear of 125 Baker Street CSO | 017081381 | WIG0239 | SO | CSO on Sewer Network | SD5747004880 | GB112070061610 | Poolstock Brook | POOLSTOCK BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 124.2 | 29 | 100%
United Utilities | REAR OF 25 WHEATFIELD CLOSE CSO | The rear of 25 Wheatfield Close CSO | 016881729 | WIR0121 | SO | CSO on Sewer Network | SJ2761089730 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | n/a | n/a | Commissioned in 2017 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 4: No cost beneficial solution | Investigation now complete, remedial work due
United Utilities | REAR OF 256 DALES BROW CSO | Rear of 256 Dales Brow CSO | 016982884 | SAL0184 | SO | CSO on Sewer Network | SD7705900757 | GB112069061430 | Folly Brook and Salteye Brook. | DEANS BROOK TRIB FOLLY BK | N/A | N/A | Commissioned in 2019 - full year data expected | 30.17 | 35 | 97.9%
United Utilities | REAR OF 34 DINELY STREET CSO | Rear of 34 DINELY STREET CSO | 01HYN0023 | HYN0023 | SO | CSO on Sewer Network | SD7452028880 | GB112071065040 | Hyndburn | RIVER HYNDBURN | N/A | N/A | Commissioned in 2019 - full year data expected | 15.1 | 8 | 93.93%
United Utilities | REAR OF 36 PETER STREET | Alleyway Adjacent to Rear of Peter Street CSO | 01VRY0095 | VRY0095 | SO | CSO on Sewer Network | SJ6679074220 | GB112068060370 | Wade Brook | WADE BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 1.9 | 9 | 100%
United Utilities | REAR OF 47 VENDALE AVE CSO (379AE) | Rear of 47 Vendale Avenue | 016982746 | SAL0162 | SO | CSO on Sewer Network | SD7695000600 | GB112069061430 | Folly Brook and Salteye Brook. | DEANS BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | REAR OF 489 MANCHESTER ROAD CSO | Rear of 489 Manchester Road CSO | 01HYN0053 | HYN0053 | SO | CSO on Sewer Network | SD7688026530 | GB112071065040 | Hyndburn | WOODNOOK WATER VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | REAR OF 65 FULTON AVE CSO 5130R | Rear of 65 Fulton Avenue CSO | 016881738 | WIR0136 | SO | CSO on Sewer Network | SJ2313087300 | GB112068060530 | The Birket including Arrowe Brook and Fender | NEWTON BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 31.33 | 13 | 100%
United Utilities | REAR OF 68 WHITBARROW RD | Rear of 68 Whitbarrow Road | 016982698 | WAR0106 | SO | CSO on Sewer Network | SJ6751087830 | 169 | #N/A | TRIB M/CHESTER SHIP CANAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | REAR OF KEATS AVENUE CSO | Rear of Keats Avenue CSO | 017081380 | WIG0226 | SO | CSO on Sewer Network | SD5734004570 | GB112070061600 | Smithy Brook | SMITHY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 54.47 | 16 | 100%
United Utilities | REAR OF KENNEDY WAY CSO | Rear of Kennedy Way CSO | 016993677 | TAM0073 | SO | CSO on Sewer Network | SJ9158094450 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 159.93 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | REAR OF KNOWLE HOUSE | Rear of Knowle House CSO | 01MAC0048 | MAC0048 | SO | CSO on Sewer Network | SJ8519083240 | GB112069061360 | Dean (Bollington to Bollin) | TRIB RIVER DEAN | N/A | N/A | Commissioned in 2019 - full year data expected | 204.33 | 65 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | REAR OF LUNAR CARAVANS | Rear of Lunar Caravans CSO | 017081263 | SRI0055 | SO | CSO on Sewer Network | SD5481025120 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 22.9 | 26 | 100%
United Utilities | REAR OF NO.4 RIBBLE AVENUE CSO | REAR OF No4 RIBBLE AVENUE CSO | 01RIB0007 | RIB0007 | SO | CSO on Sewer Network | SD7590045150 | GB112071065612 | Ribble DS Stock Beck | CULVERTED GRINDLETON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 79.83 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | REAR OF PIRELLI FACTORY CSO | Rear of Pirelli Factory CSO | 017680351 | CAR0088 | SO | CSO on Sewer Network | NY3937053450 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Commissioned in 2020 - full year data expected | 15.87 | 25 | 100%
United Utilities | REAR OF SUNNYSIDE TERRACE CSO | Rear of Sunnyside Terrace CSO | 017280303 | WYR0067 | SO | CSO on Sewer Network | SD3717047380 | 180 | #N/A | TRIBUTARY OF COCKERS DYKE | LUNE (BROADFLEET) | Fleetwood | Commissioned in 2016 - full year data expected | 9.47 | 4 | 100%
United Utilities | RED BROW CSO (42076) | Red Brow Wood CSO | NPSWQD010717 | STH0071 | SO | CSO on Sewer Network | SJ5770494436 | GB112069061220 | Millingford (Newton) Brook | SANKEY CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 354.36 | 71 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | REDEARTH ROAD/SUDELL ROAD CSO | REDEARTH ROAD / SUDELL ROAD CSO | 01BBN0124 | BBN0124 | SO | CSO on Sewer Network | SD6935022090 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 4.3 | 31 | 90.48%
United Utilities | REDVALES ROAD CSO | Redvales Road CSO | 01BRY0024 | BRY0024 | SO | CSO on Sewer Network | SD8028008430 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL VIA CULVERT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | REEDYFORD RD CSO (32020) | Reedyford Road CSO | 017180619 | PEN0080 | SO | CSO on Sewer Network | SD8634038560 | GB112071065130 | Walverden Water | CULVRTD TRIB OF WALVERDEN WTR | N/A | N/A | Commissioned in 2020 - full year data expected | 7.93 | 10 | 100%
United Utilities | REEMAN COURT MANHOLE H4 CSO 272NY | Reeman Court (Manhole H4) | EPRJB3298WZ | MAC0066 | SO | CSO on Sewer Network | SJ8449382562 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | n/a | n/a | Commissioned in 2018 - full year data expected | 97.03 | 31 | 99.92%
United Utilities | REGENT ROAD (BOLTON) CSO | Regent Road | EPRQB3499VB | BOL0024 | SO | CSO on Sewer Network | SD6732008590 | GB112069064540 | Middle Brook | BESSY BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 88.17 | 50 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RENWICK CSO (171MD) | Renwick CSO | 017680333 | EDE0084 | SO | CSO on Sewer Network | NY5954043250 | GB102076073840 | Raven Beck | HARBERRY BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.93 | 4 | 77% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | REVIDGE RD/PRESTON NEW RD SSO | Revidge Road/Preston New Road | 017180474 | BBN0149 | SO | CSO on Sewer Network | SD6622028840 | GB112071065300 | Darwen - conf Roddlesworth to tidal | TRIB ARLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | RIBBLESDALE DRIVE PS | Ribblesdale Drive PS | 017280304 | WYR0068 | SO | Storm Discharge at Pumping Station | SD4876051400 | GB112072065880 | Cocker (Lune) | TRIB RIVER COCKER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | RIBBLETON LANE CSO 33103 | Ribbleton Lane CSO | 017160312 | PRE0004 | SO | CSO on Sewer Network | SD5528028740 | 176 | #N/A | RIVER RIBBLE TIDAL VIA SWS | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 177.45 | 21 | 100%
United Utilities | RIBCHESTER WWTW | RIBCHESTER WwTW | 017160043 | 17160043 | ST | Storm Tank at WwTW | SD6516034401 | GB112071065500 | Ribble - conf Calder to tidal | RIVER RIBBLE | n/a | n/a | Commissioned in 2018 - full year data expected | 5016.45 | 210 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - August
United Utilities | RIBCHESTER WWTW | RIBCHESTER WwTW | 017160043 | 17160043 | SO | Inlet CSO at WwTW | SD6516034401 | GB112071065500 | Ribble - conf Calder to tidal | RIVER RIBBLE | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | RIBTON MOORSIDE CSO | Ribton Moorside CSO | 017480288 | COP0085 | SO | CSO on Sewer Network | NX9854016890 | 356 | #N/A | CULVERTED SEC OF SNEBRA BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.2 | 1 | 100%
United Utilities | RICKERBY CSO | Rickerbys CSO | 017680296 | CAR0002 | SO | CSO on Sewer Network | NY3997055031 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | RICKERBY PARK CSO | Rickerby Park CSO | 017680310 | CAR0060 | SO | CSO on Sewer Network | NY4055056980 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Commissioned in 2016 - full year data expected | 24.41 | 2 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | RIDDING LANE CSO (342X5) | Ridding Lane Combined Sewage Overflow | 017160332 | RIB0043 | SO | CSO on Sewer Network | SD7235036310 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 643.83 | 88 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RILSHAW LANE | Rilshaw Lane PS | 016881540 | VRY0044 | SO | Storm Discharge at Pumping Station | SJ6703065880 | GB112068060460 | Weaver (Marbury Brook to Dane) | DITCH COURSE | N/A | N/A | Commissioned in 2020 - full year data expected | 109.32 | 115 | 99.93% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RIMROSE BROOK CSO | Rimrose Brook CSO | 016931012 | SEF0105 | SO | CSO on Sewer Network | SJ3180095800 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 8.31 | 24 | 100%
United Utilities | RISHTON LANE/WESTON STREET CSO | Rishton Lane CSO | 016983269 | BOL0127 | SO | CSO on Sewer Network | SD7182007680 | GB112069064540 | Middle Brook | JENNY BECK, A TRIB OF RV CROAL | N/A | N/A | Commissioned in 2019 - full year data expected | 143.81 | 65 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | #N/A | Rishton Tank CSO | 017160074 | HYN0003 | SO | CSO on Sewer Network | SD7222030640 | GB112071065070 | Hyndburn Brook - Lower | LIVERPOOL & LEEDS CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 128.34 | 60 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RIVACRE VALLEY PARK CSO | Rivacre Valley Park CSO | 016891627 | ELL0007 | SO | CSO on Sewer Network | SJ3853077990 | GB112068060350 | Rivacre Brook | RIVACRE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 216.3 | 86 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | RIVACRE VALLEY PARK CSO | Rivacre Valley Park CSO (182OG) (ELL0010) | 01ELL0010 | ELL0010 | SO | CSO on Sewer Network | SJ3835077970 | GB112068060350 | Rivacre Brook | RIVACRE BROOK | n/a | n/a | Commissioned in 2019 - full year data expected | 107.27 | 39 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | RIVER BANK CSO | River Bank Close CSO | EPRSB3793RW | MAC0055 | SO | CSO on Sewer Network | SJ9274077660 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | n/a | n/a | Commissioned in 2018 - full year data expected | 214.83 | 89 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RIVERSIDE CSO BOLTO BOL0058 | Riverside CSO | 016950464 | BOL0058 | SO | CSO on Sewer Network | SD7633005220 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 93.99%
United Utilities | RIVERSIDE ROAD CSO | Riverside Road CSO | 01SRI0002 | SRI0002 | SO | CSO on Sewer Network | SD5307028190 | 175 | #N/A | RIVER RIBBLE | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 2.9 | 2 | 100%
United Utilities | RIVERSIDE ROAD PUMPING STATION | Riverside Road pumping station (Site ID 38026) (SEF0083) | 01SEF0083 | SEF0083 | SO | Storm Discharge at Pumping Station | SD2960003650 | GB531206908300 | ALT | RIVER ALT ESTUARINE WATERS | RIBBLE | Formby | Commissioned in 2016 - full year data expected | 11.19 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ROA ISLAND PUMPING STATION | Roa Island PS | 017480366 | BRW0102 | SO | Storm Discharge at Pumping Station | SD2318164600 | 342 | #N/A | PIEL CHANNEL | ROOSEBECK_E | Walney | Commissioned in 2016 - full year data expected | 492.74 | 131 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ROACHES LOCK CSO | Roaches Lock | 016940369 | TAM0035 | SO | CSO on Sewer Network | SD9796003130 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 44.47 | 34 | 100%
United Utilities | ROBIN HOOD CLIFTON PUMPING STATION | Robin Hood (Clifton) PS | 016993828 | SAL0031 | SO | Storm Discharge at Pumping Station | SD7845003556 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 35.83 | 13 | 100%
United Utilities | ROBIN HOOD PS | Robin Hood PS | 016993569 | WIG0142 | SO | Storm Discharge at Pumping Station | SJ6468098300 | GB112069064520 | Hey/Borsdane Brook | COP BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 73.31 | 66 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ROBIN HOOD PS | Robin Hood PS | 016993569 | WIG0142 | SO | Storm Discharge at Pumping Station | SJ6468098300 | GB112069064520 | Hey/Borsdane Brook | COP BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 89.39 | 23 | 100% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ROBIN HOOD PUMPING STATION | Robin Hood PS | 017091516 | CHR0046 | SO | Storm Discharge at Pumping Station | SD5062016350 | GB112070064920 | Syd Brook | UNNAMED TRIB OF SYD BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 557.04 | 60 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ROCHDALE RD/COLLYHURST | Rochdale Road/Alfreton Street CSO | 016993740 | MAN0116 | SO | CSO on Sewer Network | SD8533000020 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 4.6 | 12 | 100%
United Utilities | ROCHDALE RD/COLLYHURST | Rochdale Road/Collyhurst CSO | 016993740 | MAN0150 | SO | CSO on Sewer Network | SD8533000020 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | ROCHDALE ROAD/EGGINGTON STREET CSO | ROCHDALE ROAD / EGGINGTON STREET CSO | 01MAN0058 | MAN0058 | SO | CSO on Sewer Network | SD8543000100 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 87.65% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | ROCHDALE ROAD/WASH LANE SSO | Willow Street/Rochdale Road | 016951425 | BRY0126 | SO | CSO on Sewer Network | SD8186010590 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 1.43 | 11 | 100%
United Utilities | ROCHDALE WWTW | Rochdale Wastewater Treatment Works (ROCHD) (016950041) | 016950041 | 16950041 | ST | Storm Tank at WwTW | SD8816012370 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 1981.97 | 122 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | ROCHDALE/COLLYHURST ROAD CSO | Rochdale/Collyhurst Road CSO | 01MAN0050 | MAN0050 | SO | CSO on Sewer Network | SD8545000080 | GB112069061131 | Irk (Wince to Irwell) | CULV'TED SECTION OF MOSS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 22.37 | 26 | 100%
United Utilities | ROCKCLIFFE PUMPING STATION | Rockcliffe Pumping Station (Site ID RCKCL) (CAR0027) | 017680414 | CAR0027 | SO | Storm Discharge at Pumping Station | NY3578061630 | 89 | #N/A | ROCKCLIFFE BECK | Solway | n/a | Commissioned in 2017 - full year data expected | 211.46 | 81 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ROCKLIFFE ROAD/RIVER STREET CSO | ROCKCLIFFE ROAD / RIVER STREET CSO | 01ROS0015 | ROS0015 | SO | CSO on Sewer Network | SD8690022430 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.7 | 7 | 100%
United Utilities | ROCKLIFFE WWTW ROCKC | ROCKCLIFFE WwTW | 017670129 | 17670129 | ST | Storm Tank at WwTW | NY3586061080 | GB530207614700 | SOLWAY | RIVER EDEN ESTUARY | Solway | n/a | Commissioned in 2017 - full year data expected | 446.83 | 70 | 99.98% |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation
United Utilities | ROEWOODS OUTFALL SEWER | Roewoods Outfall Sewer (27206) (MAC0028) | 01MAC0028 | MAC0028 | SO | CSO on Sewer Network | SJ9030075060 | GB112069061320 | Bollin (Source to Dean) | UN-NAMED TRIB OF RIVER BOLLIN | n/a | n/a | Commissioned in 2018 - full year data expected | 63.7 | 37 | 99.99%
United Utilities | ROLLESTON AVENUE/BUTLER STREET CSO | ROLLESTON AVENUE / BUTLER STREET CSO | 01MAN0032 | MAN0032 | SO | CSO on Sewer Network | SJ8558098902 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.47 | 7 | 100%
United Utilities | ROLLS CRESCENT/YEW STREET CSO | Rolls Crescent/Yew Street CSO | 016982958 | MAN0367 | SO | CSO on Sewer Network | SJ8252097363 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 63.3 | 21 | 85.35% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | ROMNEY ROAD/TITCHFIELD STREET CSO | Romney Road/Titchfield Street CSO | 017480303 | BRW0088 | SO | CSO on Sewer Network | SD1966070554 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CROFTS BANK BROOK | WALNEY EAST | Walney West Shore | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | ROOKERY CSO | Rookery CSO (29010) (NEW0038) | 016810825 | NEW0038 | SO | CSO on Sewer Network | SJ8484055630 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | ROOKERY BROOK TRIB KIDSGROVE S | n/a | n/a | Commissioned in 2018 - full year data expected | 529.99 | 60 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ROOLEY MOOR RD W51 | Rooley Moor Road | 01ROC0077 | ROC0077 | SO | CSO on Sewer Network | SD8792014450 | GB112069064730 | Spodden | TRIB HEALEY DELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | ROSEMARY LANE CSO 252PG | Rosemary Lane CSO | 017280276 | LAN0075 | SO | CSO on Sewer Network | SD4782061820 | 178 | #N/A | MILL RACE | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 0.97 | 7 | 100%
United Utilities | ROSS LAVE LANE CSO | Ross Lave Lane CSO | 016983312 | TAM0175 | SO | CSO on Sewer Network | SJ9159094450 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | UNNAMED TRIB OF DENTON BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 179.36 | 68 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ROSSALL SCHOOL PUMPING STATION | Rossall School PS | 01WYR0007 | WYR0007 | SO | Storm Discharge at Pumping Station | SD3172045110 | 341 | #N/A | UNNAMED DYKE | Lune (Wyre Estuary) | Cleveleys | Commissioned in 2016 - full year data expected | 0.14 | 2 | 100%
United Utilities | ROSSENDALE WWTW | ROSSENDALE WwTW | 016950042 | 16950042 | ST | Storm Tank at WwTW | SD7957020610 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | ROSTHWAITE WWTW (ROSTH) | ROSTHWAITE WwTW | 017570053 | 17570053 | SO | Inlet CSO at WwTW | NY2548015050 | GB112075070330 | Derwent - headwaters to conf Stonethwaite Beck | TRIB OF RIVER DERWENT | N/A | N/A | Commissioned in 2019 - full year data expected | 127.41 | 30 | 100%
United Utilities | ROWRAH PUMPING STATION | Rowrah PS | EPRBP3420GJ | COP0035 | SO | Storm Discharge at Pumping Station | NY0611018780 | GB112075070540 | Marron | COLLIERGATE BECK | N/A | N/A | Commissioned in 2018 - full year data expected | 420.58 | 32 | 99.75%
United Utilities | ROYAL OAK CSO 07039 | Royal Oak CSO | 016983304 | BOL0129 | SO | CSO on Sewer Network | SD7347011870 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 1924.17 | 168 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ROYTON SETTLED STORM OVERFLOW | Royton Settled Storm Overflow | 016950043 | OLD0171 | SO | 0 | SD9105007100 | GB112069061161 | Irk (Sourtce to Wince Brook) | RIVER IRK (VIA LUZLEY BK) | N/A | N/A | Commissioned in 2020 - full year data expected | 699.42 | 62 | 99.99% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | RR NO 16 BRIDGEWATER ST CSO 483BR | Rear of No. 166 Bridgewater Street CSO | 01WAR0079 | WAR0079 | SO | CSO on Sewer Network | SJ6825087250 | 169 | #N/A | SLITTEN BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 162.1 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RUDD AVENUE | Rudd Avenue SSO | 016982534 | STH0066 | SO | CSO on Sewer Network | SJ5467094920 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 168.94 | 62 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RUNCORN ROAD CSO | RUNCORN ROAD CSO | 01HAL0057 | HAL0057 | SO | CSO on Sewer Network | SJ5658083671 | GB112068060520 | Keckwick Brook | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2019 - full year data expected | 211.23 | 27 | 100%
United Utilities | RUNCORN TOWN HALL CSO | Runcorn Town Hall CSO | 016881893 | HAL0133 | SO | CSO on Sewer Network | SJ5177082100 | 169 | #N/A | WILLOW BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 7.87 | 4 | 100%
United Utilities | RUNCORN WASTEWATER TREATMENT WORKS | RUNCORN WwTW | 016820127 | 16820127 | ST | Storm Tank at WwTW | SJ5412083830 | GB531206908100 | MERSEY | M/C SHIP CANAL (TIDAL) | n/a | n/a | Commissioned in 2018 - full year data expected | 935.32 | 71 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | RUSHBED SSO | Rushbed SSO | 016982214 | ROS0069 | SO | CSO on Sewer Network | SD8097024840 | GB112069064680 | Limy Water | LIMY WATER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | RUSHTON WASTEWATER TREATMENT WORKS | RUSHTON WwTW | 016810105 | 16810105 | ST | Storm Tank at WwTW | SJ5781063180 | GB112068055440 | Wettenhall Brook | TRIB WETTENHALL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 567.51 | 29 | 100%
United Utilities | S. CHADDERTON/ | South Chadderton / The Causeway Oldham CSO | 016950546 | OLD0106 | SO | CSO on Sewer Network | SD8908004340 | GB112069061120 | Wince Brook | WINCE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 285.75 | 57 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SABDEN CSO (342P9) | Sabden CSO | 01RIB0045 | RIB0045 | SO | CSO on Sewer Network | SD7691036740 | GB112071065140 | Sabden Brook | 0 | N/A | N/A | Commissioned in 2020 - full year data expected | 6.1 | 40 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | SACKVILLE ST MONTAGUE ST CSO | Sackville Street/Montague Street CSO | 01PEN0023 | PEN0023 | SO | CSO on Sewer Network | SD8414036391 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER VIA CULVERT | n/a | n/a | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | SADDLEWORTH WWTW | SADDLEWORTH WwTW | 016940090 | 16940090 | ST | Storm Tank at WwTW | SD9929004310 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 1465.39 | 80 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SALE WWTW (SALEZ) | SALE WwTW | 016940149 | 16940149 | SO | Inlet CSO at WwTW | SJ7677092920 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | SALE WWTW (SALEZ) | SALE WwTW | 016940149 | 16940149 | ST | Storm Tank at WwTW | SJ7677092920 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | SALFORD WASTEWATER TREATMENT WORKS | SALFORD WwTW | 016940150 | 16940150 | SO | Inlet CSO at WwTW | SJ7924097981 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 196.89 | 83 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting)
United Utilities | SALFORD WASTEWATER TREATMENT WORKS | SALFORD WwTW | 016940150 | 16940150 | ST | Storm Tank at WwTW | SJ7924097981 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 110.03 | 13 | 99.84%
United Utilities | SALTWORKS PUMPING STATION | ICI Saltworks PS | EPRQB3792NT | HAL0112 | SO | Storm Discharge at Pumping Station | SJ4960081800 | GB531206908100 | MERSEY | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 2.55 | 2 | 99.95%
United Utilities | SANDBACH WASTEWATER TREATMENT WORKS | SANDBACH WwTW | 016810106 | 16810106 | ST | Storm Tank at WwTW | SJ7420059290 | GB112068055420 | Wheelock (including Hassall Brook) | RIVER WHEELOCK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | SANDFORD VILLAGE WWTW | SANDFORD VILLAGE WwTW | 017680300 | 17680300 | SO | Inlet CSO at WwTW | NY7306016077 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 711.47 | 90 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SANDGATE (PENRITH) CSO (17552) | Sandgate (Penrith) CSO | 01EDE0033 | EDE0033 | SO | CSO on Sewer Network | NY5169030290 | GB102076071020 | Eamont (Upper) | THACKA BECK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 5.14 | 8 | 99.97%
United Utilities | SANDGATE PUMPING STATION NO 2 | SANDGATE PUMPING STATION | 01FYL0005 | FYL0005 | SO | Storm Discharge at Pumping Station | SD3130029500 | 350 | #N/A | THE IRISH SEA | N/A | N/A | Commissioned in 2019 - full year data expected | 0.48 | 3 | 100%
United Utilities | SANDHILLS LANE CSO | Sandhills Lane CSO | 016930970 | LIV0039 | SO | CSO on Sewer Network | SJ3320093101 | 167 | #N/A | MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 16.37 | 19 | 100%
United Utilities | SANDLE BRIDGE WW NETWORK PS | Sandle Bridge Wastewater Network PS | 016892278 | MAC0098 | SO | Storm Discharge at Pumping Station | SJ8072076830 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | PEDLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 8.88 | 2 | 99.97%
United Utilities | SANDSIDE PUMPING STATION | Sandside PS | 017370202 | LAK0057 | SO | Storm Discharge at Pumping Station | SD4779080770 | 182 | #N/A | RIVER BELA | N/A | N/A | Commissioned in 2019 - full year data expected | 1.51 | 1 | 100%
United Utilities | SANDY LANE CSO | Sandy Lane CSO | 016892357 | WIR0059 | SO | CSO on Sewer Network | SJ2905092111 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 106.49 | 78 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SANKEY BRIDGES PS | Sankey Bridge PS | 01WAR0028 | WAR0028 | SO | Storm Discharge at Pumping Station | SJ5855087620 | 170 | #N/A | SANKEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.02 | 1 | 99.64%
United Utilities | SANKEY BROOK (ST HELENS) CSO | Sankey Brook (St Helens) CSO | NPSWQD010822 | STH0005 | SO | CSO on Sewer Network | SJ5153096240 | GB112069061240 | Rainford Brook | RAINFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 34.58 | 28 | 99.99%
United Utilities | SAUGHALL MASSIE RD/DEVONSHIRE RDCSO | Saughall Massie Road / Devonshire Road CSO | 01WIR0078 | WIR0078 | SO | CSO on Sewer Network | SJ2540088540 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | N/A | Commissioned in 2016 - full year data expected | 44.47 | 23 | 99.94%
United Utilities | SAVICK BROOK PUMPING STATION | Savick Brook PS (339CT) | 01PRE0083 | PRE0083 | SO | Storm Discharge at Pumping Station | SD5031030990 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 613.9 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SAWYER BROW/VICTORA STREET CSO | SAWYER BROW / VICTORIA STREET CSO | 01TAM0080 | TAM0080 | SO | CSO on Sewer Network | SJ9560095900 | GB112069061280 | Wilson Brook | TRIBUTARY OF WILSON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.07 | 2 | 100%
United Utilities | SCALE HALL PUMPING STATION | Scale Hall PS | 017270196 | LAN0039 | SO | Storm Discharge at Pumping Station | SD4643062240 | 178 | #N/A | LUNE ESTUARY | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 5351.88 | 226 | 14.66% | Sensor failure / issue | N/A - Ongoing investigation | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - October
United Utilities | SCHNEIDER ROAD CSO | Schneider Road CSO | 017480361 | BRW0009 | SO | CSO on Sewer Network | SD1958070871 | 344 | #N/A | ORMSGILL RESERVOIR | WALNEY EAST | Walney West Shore | Commissioned in 2016 - full year data expected | 959.92 | 81 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SCHOLA GREEN LANE PS | Schola Green Lane Pumping Station | 017370197 | LAN0109 | SO | Storm Discharge at Pumping Station | SD4355063580 | GB112072065950 | Overton Dyke | MORECAMBE BAY | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 46.27 | 16 | N/A | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | SCHOOL LANE CSO | SCHOOL LANE CSO | 01SRI0019 | SRI0019 | SO | CSO on Sewer Network | SD5401022460 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 586.2 | 124 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SCHOOL LANE CSO | School Lane CSO | 01SRI0019 | FYL0006 | SO | CSO on Sewer Network | SD5401022460 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 5.03 | 22 | 99.74%
United Utilities | SCHOOL LANE/LODGE LANE CSO | School Lane/Lodge Lane CSO | 01VRY0061 | VRY0061 | SO | CSO on Sewer Network | SJ6473071330 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SCORTON VILLAGE PUMPING STATION | Gubberford Lane PS | 017260047 | WYR0049 | SO | Storm Discharge at Pumping Station | SD4998048260 | GB112072065821 | Wyre - Upper | RIVER WYRE | N/A | N/A | Commissioned in 2020 - full year data expected | 593.06 | 75 | 99.49% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SCOTBY CSO | Scotby CSO | 017670159 | CAR0017 | SO | CSO on Sewer Network | NY4330055810 | GB102076073940 | Eden - Eamont to tidal | COLLAR BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 96.53 | 20 | 100%
United Utilities | SCOTT AVENUE/HURSTEAD STREET CSO | SCOTT AVENUE / HURSTHEAD STREET CSO | 01HYN0039 | HYN0039 | SO | CSO on Sewer Network | SD7719026350 | GB112071065040 | Hyndburn | WOODNOOK WATER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SEASCALE WWTW | Seascale Wastewater Treatment Works (Site ID SEASC) (017480324) | 017480324 | 17480324 | ST | Storm Tank at WwTW | NY0403000930 | GB641211630002 | Cumbria | IRISH SEA | n/a | Seascale | Commissioned in 2017 - full year data expected | 1507.79 | 89 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SEDBERGH STW | SEDBERGH WwTW | 017270009 | 17270009 | ST | Storm Tank at WwTW | SD6512091160 | GB112072071710 | Rawthey - Lower | RIVER RAWTHEY | N/A | N/A | Commissioned in 2020 - full year data expected | 396.52 | 39 | 72.16% | Sensor failure / issue | Resolved - April
United Utilities | SEDGWICK PUMPING STATION | Sedgewick PS | 017370060 | LAK0091 | SO | Storm Discharge at Pumping Station | SD5083087230 | GB112073071460 | Kent - conf Sprint to tidal | RIVER KENT | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.96%
United Utilities | SEEDFIELD SECONDARY MODERN SCHL CSO | Seedfield Secondary Modern School CSO | 01BRY0010 | BRY0010 | SO | CSO on Sewer Network | SD8037012230 | GB112069064620 | Irwell (Rossendale STW to Roch) | UNNAMED TRIB OF RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 18.3 | 27 | 75.6% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | SEFTON AVENUE CSO (CON0090) | Sefton Avenue combined sewer overflow | EPRJB3896NC | CON0090 | SO | CSO on Sewer Network | SJ8703062334 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA S/WATER SEWER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SETTLE WASTEWATER TREATMENT WORKS | SETTLE WwTW | 017160045 | 17160045 | ST | Storm Tank at WwTW | SD8080261962 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | RIVER RIBBLE | n/a | n/a | Commissioned in 2018 - full year data expected | 785.45 | 89 | 100% |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation
United Utilities | SETTLEBECK SEDBERGH CSO | Settlebeck (Sedbergh) Combined Sewer Overflow | 01LAK0014 | LAK0014 | SO | CSO on Sewer Network | SD6639091910 | GB112072071710 | Rawthey - Lower | RIVER RAWTHEY | N/A | N/A | Commissioned in 2019 - full year data expected | 0.03 | 1 | 100%
United Utilities | SEWAGE PS 1 | Pusey Dale PS | 016920239 | CRE0019 | SO | Storm Discharge at Pumping Station | SD6133003470 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 11.83 | 3 | 100%
United Utilities | SHAKERLEY ROAD NO2 CSO | Shakerley Road No 2 CSO | 016983325 | WIG0233 | SO | CSO on Sewer Network | SD6869002250 | GB112069060810 | Bedford Brook | SHAKERLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 231.5 | 61 | 95.43% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SHAP PS | Shap (Brackenber) WwNPS | 017680338 | EDE0089 | SO | Storm Discharge at Pumping Station | NY5617014270 | GB102076070690 | Lowther (Upper) | DOCKER BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | SHAP STW | SHAP WwTW | 017670025 | 17670025 | SO | Inlet CSO at WwTW | NY5581015780 | GB102076070900 | Leith | SHAP BECK (RIVER LEITH) | N/A | N/A | Commissioned in 2019 - full year data expected | 692.07 | 40 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SHAROE GREEN HOSPITAL CSO 333JK | Sharoe Green Hospital CSO | 01PRE0012 | PRE0012 | SO | CSO on Sewer Network | SD5376031960 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 135.5 | 55 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SHAROE GREEN LANE CSO 33034 | Sharoe Green Lane combined sewer overflow (33034) (PRE0124) | EPRLP3329XW | PRE0124 | SO | CSO on Sewer Network | SD5393032010 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 68.88 | 35 | 100%
United Utilities | SHARPLES AVE EASTGROVE AVE CSO 071S | Sharples/East Grove Avenue | 01BOL0134 | BOL0134 | SO | CSO on Sewer Network | SD7154012680 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SHARPLES STREET CSO | SHARPLES STREET CSO | 01BBN0038 | BBN0038 | SO | CSO on Sewer Network | SD6795027160 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Commissioned in 2020 - full year data expected | 965.33 | 249 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SHAW LANE CSO 212Q4 | Shaw Lane CSO | 016892342 | PEA0037 | SO | CSO on Sewer Network | SK0143094980 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | GLOSSOP BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.57 | 2 | 100%
United Utilities | SHAW MAIN OUTFALL | Newhey Shaw Main Outfall CSO | 01OLD0150 | OLD0150 | SO | CSO on Sewer Network | SD9313011230 | GB112069064690 | Beal | RIVER BEAL | N/A | N/A | Commissioned in 2019 - full year data expected | 284.42 | 31 | 100%
United Utilities | SHAW ROAD CSO | Shaw Road CSO | 016982938 | ROC0172 | SO | CSO on Sewer Network | SD9326011200 | GB112069064690 | Beal | RIVER BEAL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.2 | 1 | 100%
United Utilities | SHEEPFOOT LANE CSO | SHEEPFOOT LANE CSO | 01OLD0032 | OLD0032 | SO | CSO on Sewer Network | SD9063006911 | GB112069061161 | Irk (Sourtce to Wince Brook) | PLUMPTON CLOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 240.33 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | SHERBORNE STREET CSO | Sherborne Street CSO | 016993836 | MAN0052 | SO | CSO on Sewer Network | SJ8346099322 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 79.1 | 51 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | SHERIDAN WAY CSO 44179 | Sheridan Way CSO | 01TAM0015 | TAM0015 | SO | CSO on Sewer Network | SJ9271493544 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 64.32 | 33 | 99.97% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | SHOECROFT GARAGE SITE CSO | SHOECROFT GARAGE SITE CSO | 01TAM0068 | TAM0068 | SO | CSO on Sewer Network | SJ9192094850 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 67.17 | 57 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SHORE ROAD NETWORK PUMPING STATION | Shore Road Wastewater Network PS(Site ID 49065) (WLN0008) | 01WLN0008 | WLN0008 | SO | Storm Discharge at Pumping Station | SD4375023810 | 175 | #N/A | DUNKIRK DIB | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 56.89 | 37 | 99.96%
United Utilities | SHUTTLEWORTH STCALDER ST CSO | SHUTTLEWORTH STREET / CALDER STREET CSO | 01BUR0024 | BUR0024 | SO | CSO on Sewer Network | SD7926033900 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | SILLOTH WASTEWATER TREATMENT WORKS | SILLOTH WwTW | 017570006 | 17570006 | SO | Inlet CSO at WwTW | NY1087054120 | 90 | #N/A | SOLWAY FIRTH AT SILLOTH BAY | SILLOTH | Silloth | Commissioned in 2016 - full year data expected | 81.14 | 25 | 99.99%
United Utilities | SIMONSTONE LANE CSO | Simonstone Lane CSO | EPRSB3396ES | RIB0050 | SO | CSO on Sewer Network | SD7698033350 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 8.13 | 7 | 100%
United Utilities | SINGING CLOUGH CSO 071Q8 | Singing Clough CSO | 01BOL0164 | BOL0164 | SO | CSO on Sewer Network | SD7513005210 | GB112069061451 | Irwell (Croal to Irk) | CLVRT TRIB OF RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 8.73 | 18 | 96.22%
United Utilities | SINGLETON PS | Singleton PS | 017290649 | WYR0083 | SO | Storm Discharge at Pumping Station | SD3826037940 | GB112072066120 | Hillylaid Pool - Tidal Wyre | UNNAMED TRIB OF MAIN DYKE | N/A | N/A | Commissioned in 2020 - full year data expected | 123.95 | 37 | 99.83%
United Utilities | SION STREET CSO 09026 | Sion Street CSO | 01BRY0032 | BRY0032 | SO | CSO on Sewer Network | SD7795006820 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 1952.06 | 94 | 95.78% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | SKELMERSDALE WWTW SKELM | SKELMERSDALE WwTW | 017020107 | 17020107 | SO | Inlet CSO at WwTW | SD4817412024 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 80.76 | 36 | 99.98%
United Utilities | SKELMERSDALE WWTW SKELM | SKELMERSDALE WwTW | 017020107 | 17020107 | ST | Storm Tank at WwTW | SD4817412024 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 176.87 | 22 | 99.4%
United Utilities | SKELTON PS | Skelton PS | 017680339 | EDE0090 | SO | Storm Discharge at Pumping Station | NY4327035420 | GB102076073760 | Ive | TRIB GRISE BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 70.57 | 30 | 99.99%
United Utilities | SKELTON STW | SKELTON WwTW | 017670116 | 17670116 | SO | Inlet CSO at WwTW | NY4345036380 | GB102076073760 | Ive | TRIB GRISE BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 468.72 | 68 | 99.99% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | SKIPPOOL PUMPING STATION | Skippool Pumping Station (Site ID 52560) (WYR0076) | 017260059 | WYR0076 | SO | Storm Discharge at Pumping Station | SD3582040850 | 180 | #N/A | WYRE ESTUARY | Lune (Wyre) | Fleetwood | Commissioned in 2017 - full year data expected | 901.61 | 69 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SKIRWITH HALL CSO | Skirwith Hall Combined Sewer Overflow | 01EDE0003 | EDE0003 | SO | CSO on Sewer Network | NY6134032480 | GB102076073800 | Briggle Beck | SKIRWITH BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 2.93 | 9 | 91.2%
United Utilities | SKIRWITH HALL CSO | Skirwith PS | 01EDE0003 | EDE0121 | SO | Storm Discharge at Pumping Station | NY6134032480 | GB102076073800 | Briggle Beck | SKIRWITH BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 12.15 | 4 | 99.86%
United Utilities | SLADE LANE CSO | SLADE LANE CSO | 01BUR0025 | BUR0025 | SO | CSO on Sewer Network | SD7915034490 | GB112071065490 | Calder - Pendle Water to conf Ribble | DEAN CLOUGH RIVER CALDER | N/A | N/A | Commissioned in 2019 - full year data expected | 35.03 | 22 | 100%
United Utilities | SLAIDBURN WW NTWK PUMPING STATION | Slaidburn PS | 01RIB0003 | RIB0003 | SO | Storm Discharge at Pumping Station | SD7131052270 | GB112071065350 | Hodder - conf Croasdale Bk to conf Easington Bk | RIVER HODDER | N/A | N/A | Commissioned in 2020 - full year data expected | 65.48 | 8 | 99.98%
United Utilities | SLAIDBURN WWTW | SLAIDBURN WwTW | 017160046 | 17160046 | SO | Inlet CSO at WwTW | SD7090051410 | GB112071065350 | Hodder - conf Croasdale Bk to conf Easington Bk | RIVER HODDER | n/a | n/a | Commissioned in 2018 - full year data expected | 459.7 | 35 | 99.42%
United Utilities | SLEDMOOR ROAD CSO | Sledmoor Road CSO | 016982979 | MAN0387 | SO | CSO on Sewer Network | SJ8141091950 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SMEDLEY ROAD CSO | Smedley Road CSO | 01MAN0042 | MAN0042 | SO | CSO on Sewer Network | SD8524000350 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 63.09 | 30 | 99.95%
United Utilities | SMITH BRIDGE ROAD CSO 35051 | Smithy Bridge Road CSO | 01ROC0122 | ROC0122 | SO | CSO on Sewer Network | SD9241015390 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 263.5 | 26 | 100%
United Utilities | SMITH ST AND JOHN ST CSO 35021 | Junction of Smith Street/John Street CSO | 016993536 | ROC0039 | SO | CSO on Sewer Network | SD9011013440 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 38.11 | 45 | 99.93% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SMITHY LANE PUMPING STATION 19003 | Smithy Lane PS | 01FYL0011 | FYL0011 | SO | Storm Discharge at Pumping Station | SD3420029400 | GB112071065650 | Liggard Brook | UNNAMED TRIB LAGGARD BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | SNEBRA WHITEHAVEN CSO 023B2 | Snebra Whitehaven CSO | 01COP0039 | COP0039 | SO | CSO on Sewer Network | NX9831016730 | 356 | #N/A | TRIB OF POW BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.27 | 1 | 100%
United Utilities | SNIPE CLOUGH CSO | Snipe Clough CSO | 016982237 | OLD0100 | SO | CSO on Sewer Network | SD9374903315 | GB112069061151 | Medlock (Source to Lumb Brook) | GLODWICK BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 244.53 | 93 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SOCKBRIDGE AND TIRRIL WWTW SOCKB | SOCKBRIDGE & TIRRIL WwTW | 017670087 | 17670087 | SO | Inlet CSO at WwTW | NY5014027080 | GB102076071020 | Eamont (Upper) | LADY BECK TRIB RIVER EAMONT | n/a | n/a | Commissioned in 2018 - full year data expected | 101.6 | 39 | 98.65%
United Utilities | SOUTERGATE VILLAGE PUMPING STATION | Soutergate Village Pumping Station (Site ID SOUPS) (LAK0094) | 017480359 | LAK0094 | SO | Storm Discharge at Pumping Station | SD2205081371 | 187 | #N/A | SOUTERGATE BECK | Duddon and Walney | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 5.08 | 4 | 99.94%
United Utilities | SOUTERGATE WWTW SOUTE SOUTE | SOUTERGATE WwTW | 017470020 | 17470020 | SO | Inlet CSO at WwTW | SD2205081370 | 187 | #N/A | SOUTERGATE BECK | Duddon and Walney | Haverigg, Walney Biggar Bank, Walney West Shore, and Walney Sandy Gap | Commissioned in 2017 - full year data expected | 634.33 | 84 | 99.89% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SOUTH EAST OF NEWTON SSO | SE Newton | 017370140 | BRW0073 | SO | Storm Discharge at Pumping Station | SD2342071280 | 342 | #N/A | SARAH BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SOUTH OF BALL STREET CSO | WIG0165A South of Ball Street CSO | NPSWQD003177 | WIG0165A | SO | CSO on Sewer Network | SD5635706786 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS VIA SWS | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SOUTH OF BLACKLEY NEW ROAD CSO | BLACKLEY NEW ROAD CSO | 01MAN0111 | MAN0111 | SO | CSO on Sewer Network | SD8390003150 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2018 - full year data expected | 76.2 | 78 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SOUTH OF BLACKLEY NEW ROAD CSO | Blackley New Road CSO | 016993799 | MAN0110 | SO | CSO on Sewer Network | SD8390003150 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 18.22 | 16 | 99.89%
United Utilities | SOUTH OF BLACKLEY NEW ROAD CSO | South Blackley New Road CSO | 016993799 | MAN0347 | SO | CSO on Sewer Network | SD8390003150 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.1 | 1 | 100%
United Utilities | SOUTH OF OLD LANGHO RD CSO | South of Old Langho Road CSO | 01RIB0019 | RIB0019 | SO | CSO on Sewer Network | SD7066536133 | GB112071065490 | Calder - Pendle Water to conf Ribble | UNNAMED TRIB OF BUSHBURN BROOK | N/A | N/A | Commissioned in 2017 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SOUTH OF PEEL TERRACE CSO | South of Peel Terrace, Chester Road, MHT (Outlet 2) | 01TRA0052 | TRA0052 | SO | CSO on Sewer Network | SJ7945093410 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SOUTH OF PEEL TERRACE CSO | South of Peel Terrace CSO | 01TRA0051 | TRA0051 | SO | CSO on Sewer Network | SJ7945093410 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIV. MERSEY/KICKETY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 97.44%
United Utilities | SOUTH PARADE CSO 202S2 | South Parade CSO | 01HAL0106 | HAL0106 | SO | CSO on Sewer Network | SJ4963081130 | GB531206908100 | MERSEY | WEAVER NAVIGATION | n/a | n/a | Commissioned in 2018 - full year data expected | 0.2 | 3 | 100%
United Utilities | SOUTH PARK HALL/STOCKS LANE HESKIN | SOUTH PARK HALL / STOCKS LANE HESKIN CSO | 01CHR0012 | CHR0012 | SO | CSO on Sewer Network | SD5336015480 | GB112070064920 | Syd Brook | SYD BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SOUTH STREET/PICKUP STREET CSO | SOUTH STREET / PICKUP STREET CSO | 01ROS0020 | ROS0020 | SO | CSO on Sewer Network | SD8694022940 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.3 | 3 | 100%
United Utilities | SOUTHERN RELIEF CSO | Southern Relief CSO | 016930984 | LIV0051 | SO | CSO on Sewer Network | SJ3835085050 | 167 | #N/A | MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 211.04 | 62 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SOUTHPORT WWTW | SOUTHPORT WwTW | 017030100 | 17030100 | ST | Storm Tank at WwTW | SD3708020820 | 173 | #N/A | CROSSENS POOL | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2017 - full year data expected | 207.29 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SOUTHWAITE PS | Southwaite PS | 017680340 | EDE0091 | SO | Storm Discharge at Pumping Station | NY4499045170 | GB102076074030 | Petteril d/s Blackrack Beck | TRIB RIVER PETTERIL | N/A | N/A | Commissioned in 2019 - full year data expected | 37.91 | 11 | 99.83%
United Utilities | SOUTHWAITE WWTW | SOUTHWAITE WwTW | 017670112 | 17670112 | SO | Inlet CSO at WwTW | NY4495046350 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | SOW BROOK PS | Sow Brook PS | 016982211 | WAR0097 | SO | Storm Discharge at Pumping Station | SJ6823087820 | 169 | #N/A | SOW BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 195.93 | 20 | 99.96%
United Utilities | SPA ROAD CSO 07017 | Spa Road CSO | 016982192 | BOL0172 | SO | CSO on Sewer Network | SD7070009100 | GB112069064540 | Middle Brook | RIVER CROAL | n/a | n/a | Commissioned in 2020 - full year data expected | 1009.84 | 79 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SPA ROAD CSO 07017 | Walker Street | 016982192 | BOL0188 | SO | CSO on Sewer Network | SD7070009100 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Commissioned in 2020 - full year data expected | 4.1 | 9 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SPARK BRIDGE PUMPING STATION | Spark Bridge Wastewater Network Pumping Station | EPRBP3624XL | LAK0108 | SO | Storm Discharge at Pumping Station | SD3068084701 | GB112073071190 | Crake | RIVER CRAKE | N/A | N/A | Commissioned in 2020 - full year data expected | 1211.27 | 87 | 99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SPENCER STREET/DARWIN STREET CSO | SPENCER STREET / DARWIN STREET CSO | 01VRY0067 | VRY0067 | SO | CSO on Sewer Network | SJ6559073060 | GB112068060460 | Weaver (Marbury Brook to Dane) | WEAVER NAVIGATION VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 5.97 | 17 | 100%
United Utilities | SPIKE ISLAND ACCESS RD CSO (202RW) | SPIKE ISLAND ACCESS ROAD CSO | 01HAL0053 | HAL0053 | SO | CSO on Sewer Network | SJ5165084740 | GB531206908100 | MERSEY | BOWERS BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 4.9 | 10 | 100%
United Utilities | SPOTLAND BRIDGE CSO 35035 | Spotland Bridge CSO | 016981350 | ROC0099 | SO | CSO on Sewer Network | SD8861013830 | GB112069064730 | Spodden | RIVER SPODDEN | n/a | n/a | Commissioned in 2018 - full year data expected | 285.11 | 80 | 82.54% | Sensor failure / issue | Resolved - November | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SPRAGG ST WILLOW ST CSO CON0089 | Spragg Street/ Willow Street CSO | EPRJB3896RV | CON0089 | SO | CSO on Sewer Network | SJ8630863019 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SPRING GARDENS WADDINGTON CSO | Spring Gardens(Waddington) CSO | 01RIB0004 | RIB0004 | SO | CSO on Sewer Network | SD7306043500 | GB112071065612 | Ribble DS Stock Beck | WADDINGTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 140.23 | 63 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | SPRING VALE COMBINED SEWER OVERFLOW | Spring Vale CSO | 016982642 | ROC0166 | SO | CSO on Sewer Network | SD8753006030 | GB112069061161 | Irk (Sourtce to Wince Brook) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 17.67 | 8 | 100%
United Utilities | SPRINGFIELD ROAD CSO | Springfield Road CSO | 01WIG0004 | WIG0004 | SO | CSO on Sewer Network | SD5624006711 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 7.03 | 29 | 100%
United Utilities | SPRINGFIELD TANK CSO | Springfield Tank CSO | 01BOL0174 | BOL0174 | SO | CSO on Sewer Network | SD7230008930 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.23 | 3 | 100%
United Utilities | SQUIRES GATE LANE | Squires Gate Lane | 01BPL0020 | BPL0020 | SO | CSO on Sewer Network | SD3279032320 | GB112071065651 | Main Drain (Ribble) | SQUIRES GATE LANE DYKE | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | SSO ADJ CROSS KEYS INN | Adjacent Cross Keys Inn | 017280324 | EDE0104 | SO | CSO on Sewer Network | NY6164004390 | GB112072071720 | Lune - conf Birk Beck to conf Rawthey | TRIB RIVER LUNE | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | ST ANDREWS RD BROOKS AV CSO 09001 | Junction of St Andrews Road/Brooks Avenue CSO | 016993585 | BRY0025 | SO | CSO on Sewer Network | SD7786008710 | GB112069060840 | Irwell (Roch to Croal) | BLACK LANE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 38.69 | 8 | 100%
United Utilities | ST ANDREWS ROAD/ST MICHAEL CSO | St Andrew's Road/St Michael's Road CSO | 01SEF0012 | SEF0012 | SO | CSO on Sewer Network | SD2955001654 | 348 | #N/A | MERSEY ESTUARY | NORTH WIRRAL (EAST) | Formby | Commissioned in 2016 - full year data expected | 227.47 | 86 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ST ANNES CRICKET GROUND SPS | St Anne's Square | 017190384 | OLD0138 | SO | CSO on Sewer Network | SD3214030300 | GB112071065650 | Liggard Brook | TRIB MAIN DRAIN | n/a | n/a | Commissioned in 2018 - full year data expected | 355.17 | 70 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ST BEES PUMPING STATION | St Bees PS | 017480322 | COP0097 | SO | CSO on Sewer Network | NX9690011400 | GB112074069990 | Pow Beck (South West Lakes) | POW BECK | n/a | St Bees | Commissioned in 2017 - full year data expected | 679.01 | 59 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ST BRIDGETS LANE CSO | St Bridgets Lane CSO | 01COP0027 | COP0027 | SO | CSO on Sewer Network | NY0097010620 | GB112074069980 | Ehen (lower) | CULV'T'D SECT OF SKIRTING BECK | N/A | St Bees | Commissioned in 2016 - full year data expected | 0.1 | 1 | 100%
United Utilities | ST GEORGE STREET/HANOVER STREET CSO | St. George Street/Hanover Street CSO | 01TAM0118 | TAM0118 | SO | CSO on Sewer Network | SJ9591098541 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | ST GEORGES ROAD CSO | St George's Road CSO | 017160320 | PRE0024 | SO | CSO on Sewer Network | SD5482030450 | 176 | #N/A | MOORE BROOK CULVERT | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 3.73 | 10 | 100%
United Utilities | ST HELENS CLOSE CSO | ST HELENS CLOSE CSO | 01WAR0047 | WAR0047 | SO | CSO on Sewer Network | SJ7015091300 | GB112069061420 | Glaze | RIVER GLAZE VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 677.67 | 111 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ST HELENS ROAD CSO 422SZ | St Helens Road CSO | 016982537 | STH0067 | SO | CSO on Sewer Network | SJ4852093690 | GB112069061210 | Hardshaw (Windle) Brook | UNNAMED TRIB OF ECCLESTON MERE | n/a | n/a | Commissioned in 2018 - full year data expected | 203.17 | 110 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ST HELENS STW | St Helens Wastewater Treatment Works (Site STHEL) (016920130) | 016920130 | 16920130 | ST | Storm Tank at WwTW | SJ5358095920 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1422.68 | 110 | 100% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled
United Utilities | ST HELENS STW | St Helens Wastewater Treatment Works (Site STHEL) (016920130) | 016920130 | 16920130 | SO | Inlet CSO at WwTW | SJ5358095920 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 122.05 | 48 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ST JOHNS RD | St Johns Road CSO | 01BOL0074 | BOL0074 | SO | CSO on Sewer Network | SD6697007750 | GB112069064540 | Middle Brook | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | HAVANNAH STREET/ REDFERN AVE CSO | Havannah Street/Redfern Avenue Combined Sewer Overflow | 016892194 | CON0037 | SO | CSO on Sewer Network | SJ8678763891 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Commissioned in 2019 - full year data expected | 18.23 | 23 | 100%
United Utilities | ST JOHNS WOOD CSO 272S9 | St Johns Road CSO | 01MAC0026 | MAC0026 | SO | CSO on Sewer Network | SJ7692079330 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | BIRKIN BROOK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 188.17 | 107 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ST MARYS CHURCH (CHIPPING) CSO | ST MARYS CHURCH CSO | 01RIB0005 | RIB0005 | SO | CSO on Sewer Network | SD6236043300 | GB112071065330 | Chipping Brook | CHIPPING BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 10.83 | 15 | 100%
United Utilities | ST MARYS GATE/CHEETHAM STREET CSO | St. Mary's Gate / Cheetham Street CSO | EPRQB3591EA | ROC0055 | SO | CSO on Sewer Network | SD8974013730 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | JOHNSON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 4.03 | 15 | 100%
United Utilities | ST MARYS RD COMBINED SEWER OVERFLOW | CSO opposite No. 62 St Mary's Road | 016993589 | PEA0033 | SO | CSO on Sewer Network | SK0311093940 | GB112069060730 | Glossop (Shelf) Brook (Source to Long Clough Brook) | GLOSSOP BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 12.57 | 14 | 100%
United Utilities | ST MARY'S ROAD CSO | ST MARYS ROAD CSO | 01WIG0018 | WIG0018 | SO | CSO on Sewer Network | SD6092007880 | GB112070061610 | Poolstock Brook | TRIB. OF INCE BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 790.2 | 113 | 80.87% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | ST MICHAELS ROAD/MANOR ROAD CSO | St Michaels Road/Manor Road CSO | 01SEF0013 | SEF0013 | SO | CSO on Sewer Network | SD2955001655 | 348 | #N/A | RIVER ALT (TIDAL) | NORTH WIRRAL (EAST) | Formby | Commissioned in 2016 - full year data expected | 733.03 | 111 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ST MICHAELS WAY CSO | St. Michael's Way Combined Sewer Overflow (Site ID 132TH) (CON0039) | 01CON0039 | CON0039 | SO | CSO on Sewer Network | SJ6946066700 | GB112068055380 | Wheelock (Fowle Brook to Dane) | RIVER WHEELOCK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 26.53 | 37 | 100%
United Utilities | ST NICHOLAS LANE PUMPING STATION | St Nicholas Lane Pumping Station (Site ID STNIC) (LAN0057) | 017190855 | LAN0057 | SO | Storm Discharge at Pumping Station | SD4782068760 | 185 | #N/A | MILL DAM | Morecambe Bay East | Morecambe North and Morecambe South | Commissioned in 2017 - full year data expected | 114.03 | 55 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ST NICHOLAS LANE PUMPING STATION | St. Nicholas Storm Sewer overflow | 017190855 | LIV0027 | SO | CSO on Sewer Network | SD4782068760 | 185 | #N/A | MILL DAM | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2017 - full year data expected | 3.98 | 8 | 100%
United Utilities | ST PAULS ROAD CSO | St Pauls Road CSO | 017190769 | WIR0138 | SO | CSO on Sewer Network | SD5418030480 | 176 | #N/A | RIVER RIBBLE ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 106.63 | 61 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | ST PAUL'S ROAD CSO | St Paul's Road combined sewer overflow (332TX) (PRE0006) | 016881649 | PRE0006 | SO | CSO on Sewer Network | SJ3306087130 | 171 | #N/A | THE MERSEY ESTUARY | n/a | n/a | Commissioned in 2018 - full year data expected | 4136.87 | 175 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled
United Utilities | ST WERBURGHS RD CSO SITE 282T5 | St Werbughes Road / Sandy Lane CSO | 01MAN0232 | MAN0232 | SO | CSO on Sewer Network | SJ8234093340 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.1 | 1 | 100%
United Utilities | STAINTON (SNUFF MILL) SSO | Stainton SSO | 017680275 | EDE0080 | SO | CSO on Sewer Network | NY4906027430 | GB102076071020 | Eamont (Upper) | RIVER EAMONT | N/A | N/A | Commissioned in 2019 - full year data expected | 714.65 | 47 | 96.18% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STAMFORD GROVE CSO | STAMFORD GROVE CSO | 01TAM0102 | TAM0102 | SO | CSO on Sewer Network | SJ9565098980 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME VIA A CULVERT | N/A | N/A | Commissioned in 2020 - full year data expected | 0.1 | 2 | 96.74%
United Utilities | STAMFORD NEW ROAD CSO | Stamford New Road CSO | 016892328 | TRA0032 | SO | CSO on Sewer Network | SJ7739088340 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 93.26 | 70 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STAMFORD ROAD CSO | STAMFORD ROAD CSO | 01TAM0087 | TAM0087 | SO | CSO on Sewer Network | SD9716002650 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | COUNTY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | STAMFORD ST CSO (442SC) | Stamford Street CSO | 016993724 | TAM0094 | SO | CSO on Sewer Network | SJ9789099680 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | SWINESHAW BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.57 | 4 | 100%
United Utilities | STAMPERY WWN PUMPING STATION | Stampery PS | 017570092 | ALL0075 | SO | Storm Discharge at Pumping Station | NY2574049030 | GB102075073390 | Wiza Beck | SPEET GILL | N/A | N/A | Commissioned in 2019 - full year data expected | 375.52 | 55 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STAND LANE CSO 09058 | Stand Lane CSO | 01BRY0036 | BRY0036 | SO | CSO on Sewer Network | SD7863006940 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 342.12 | 99 | 99.05% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STANDEDGE RD DIGGLE SSO | Standedge Road SSO | 016982528 | OLD0016 | SO | CSO on Sewer Network | SD9985006900 | GB112069064741 | Tame (Source to Chew Brook) | DIGGLE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | STANLEY AVENUE/GREEN LANE CSO | Stanley Green Avenue/Green Lane CSO | 016881737 | WIR0135 | SO | CSO on Sewer Network | SJ2902092720 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER BIRKET | N/A | N/A | Commissioned in 2016 - full year data expected | 2.13 | 7 | 100%
United Utilities | STANLEY AVENUE/GREEN LANE CSO | Stanley Road Pumping Station (Site ID 51005) (WIR0090) | 016881737 | WIR0090 | SO | Storm Discharge at Pumping Station | SJ2902092720 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER BIRKET | Dee (East) and North Wirrall (West) | West Kirby and Meols | Commissioned in 2016 - full year data expected | 0 | 0 | 100%
United Utilities | STANNEY ROAD CSO | Stanney Road CSO | NPSWQD010735 | ROC0051 | SO | CSO on Sewer Network | SD9127013620 | GB112069064720 | Roch (Source to Spodden) | STANNEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 8.23 | 6 | 100%
United Utilities | STANTON ROAD PS | Stanton Road PS | 01WIR0106 | WIR0106 | SO | Storm Discharge at Pumping Station | SJ3244083410 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | BOARDMAN BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | STANWIX/STAINTON CSO | Stanwix and Stainton combined sewer overflow (Site ID 10009) (CAR0055) | 017670218 | CAR0055 | SO | CSO on Sewer Network | NY3805056520 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | Solway | N/A | Commissioned in 2018 - full year data expected | 210.47 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | STATION HILL CSO | Station Hill CSO | 017580225 | ALL0091 | SO | CSO on Sewer Network | NY2539048820 | GB102075073390 | Wiza Beck | WIZA BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 50.7 | 20 | 100%
United Utilities | STATION RD COMBINED SEWER OVERFLOW | Station Road CSO | 016881580 | WIR0117 | SO | CSO on Sewer Network | SJ2915091650 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2020 - full year data expected | 9.24 | 18 | 99.97%
United Utilities | STATION RD COMBINED SEWER OVERFLOW | POW Bridge/Station Road CSO | 016881580 | COP0036 | SO | CSO on Sewer Network | SJ2915091650 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | N/A | St Bees | Commissioned in 2016 - full year data expected | 2.5 | 3 | 100%
United Utilities | STATION ROAD (PALIHAM) CSO | Station Road (Padiham) CSO | 01BUR0018 | BUR0018 | SO | CSO on Sewer Network | SD7937033870 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 234 | 87 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STATION ROAD (WHITWORTH) CSO | Station Road (Whitworth) CSO | 01ROS0044 | ROS0044 | SO | CSO on Sewer Network | SD8804016380 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Commissioned in 2020 - full year data expected | 7.27 | 5 | 100%
United Utilities | STATION ROAD CSO | STATION ROAD (Keele) CSO | 01NEW0008 | NEW0008 | SO | CSO on Sewer Network | SJ7963045770 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Commissioned in 2020 - full year data expected | 326.1 | 56 | 95.69% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STATION ROAD CSO 19084 | Station Road CSO | 017190852 | FYL0014 | SO | CSO on Sewer Network | SD4180032600 | GB112071065670 | Dow Brook | WRONGWAY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 450.12 | 38 | 98.93%
United Utilities | STAVELEY WWTW | STAVELEY WwTW | 017370061 | 17370061 | ST | Storm Tank at WwTW | SD4827098020 | GB112073071380 | Kent - conf Gowan to conf Sprint | RIVER KENT | n/a | n/a | Commissioned in 2018 - full year data expected | N/A | N/A | 0% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | STAVELEY WWTW | STAVELEY WwTW | 017370061 | 17370061 | SO | Inlet CSO at WwTW | SD4827098020 | GB112073071380 | Kent - conf Gowan to conf Sprint | RIVER KENT | n/a | n/a | Commissioned in 2018 - full year data expected | 1171.79 | 80 | 90.17% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STENKRITH BRIDGE SSO | Stenkrith Bridge CSO | 017680271 | EDE0076 | SO | CSO on Sewer Network | NY7730007470 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 173.5 | 26 | 100%
United Utilities | STEVENSON CLOSE (WORSLEY) CSO | Stevenson Close (Worsley) CSO | 017091463 | WIG0242 | SO | CSO on Sewer Network | SD5734004410 | GB112070061600 | Smithy Brook | SMITHY BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 39.33% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | STIRK HOUSE HOTEL WWPS | Stirk House Hotel PS | 017160134 | RIB0029 | SO | Storm Discharge at Pumping Station | SD8154048370 | GB112071065612 | Ribble DS Stock Beck | WHEATLEY BECK, TRIB R. RIBBLE | N/A | N/A | Commissioned in 2019 - full year data expected | 30.73 | 11 | 99.93%
United Utilities | STIRLING CLOSE CSO 508NA | Stirling Close CSO | 016993846 | WIG0244 | SO | CSO on Sewer Network | SD6790000450 | GB112069060810 | Bedford Brook | COLLING LANE BROOK, PEN LEACH | n/a | n/a | Commissioned in 2018 - full year data expected | 96.47 | 18 | 100%
United Utilities | STOCKBRIDGE ROAD CSO (BUR0038) | Stockbridge Road Burnley CSO | EPRJB3895EB | BUR0038 | SO | CSO on Sewer Network | SD7963933472 | GB112071065080 | Green Brook | GREEN BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | STOCKPORT RD ESSEX AVE CSO 432SK | Stockport Road/Essex Avenue CSO | 016982653 | STK0053 | SO | CSO on Sewer Network | SJ8776089891 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY ESTUARY VIA SWS | n/a | n/a | Commissioned in 2017 - full year data expected | 16.2 | 7 | 30.53% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | STOCKPORT RD WEST/ASHTON RD CSO | Stockport Road West/Ashton Road CSO | NPSWQD010908 | STK0003 | SO | CSO on Sewer Network | SJ9182091700 | GB112069061000 | Goyt (Etherow to Mersey) | CROOKILLEY BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.03 | 1 | 100%
United Utilities | STOCKPORT ROAD CSO | Stockport Road CSO | 01TAM0086 | TAM0086 | SO | CSO on Sewer Network | SD9705002570 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | COUNTY BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | STOCKPORT ROAD WEST CSO | Stockport Road West CSO | 01STK0012 | STK0012 | SO | CSO on Sewer Network | SJ9102091120 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.03 | 1 | 100%
United Utilities | STOCKPORT ROAD/HILL TOP DRIVE CSO | Stockport Road CSO | NPSWQD010103 | STK0149 | SO | CSO on Sewer Network | SJ9429988849 | GB112069061000 | Goyt (Etherow to Mersey) | MARPLE BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | STOCKPORT WWTW | STOCKPORT WwTW | 016940151 | 16940151 | ST | Storm Tank at WwTW | SJ8652089820 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2016 - full year data expected | 1008.19 | 124 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | STOCKPORT WWTW | STOCKPORT WwTW | 016940151 | 16940151 | SO | Inlet CSO at WwTW | SJ8652089820 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2016 - full year data expected | 399.22 | 84 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | STOCKS LANE CSO | STOCKS LANE CSO | 01TAM0113 | TAM0113 | SO | CSO on Sewer Network | SJ9741098290 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | STOCKS BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 1.5 | 6 | 99.99%
United Utilities | STONECLOUGH ROAD CSO 07045 | Singing Clough CSO | 016941213 | BOL0166 | SO | CSO on Sewer Network | SD7533005580 | GB112069061451 | Irwell (Croal to Irk) | CLVRT SINGING CLOUGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 189.1 | 61 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | STONEGARTH COMBINED SEWER OVERFLOW | STONEGARTH CSO | 01CAR0012 | CAR0012 | SO | CSO on Sewer Network | NY3821054740 | GB102076073880 | Caldew d/s Caldbeck | DOW BECK CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 247.07 | 54 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STONEHILL ROAD CSO 07049 | Stonehill Road CSO | 016982823 | BOL0193 | SO | CSO on Sewer Network | SD7378404838 | GB112069061451 | Irwell (Croal to Irk) | CULVRT SINGING CLOUGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 221.63 | 57 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STONEHILL ROAD CSO 07049 | Stonehill Road CSO | 016982823 | BOL0182 | SO | CSO on Sewer Network | SD7378404838 | GB112069061451 | Irwell (Croal to Irk) | CULVRT SINGING CLOUGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 110.94 | 50 | 99.91% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STONEHILL TRADING ESTATE CSO | Stonehill Trading Estate CSO | 016993835 | SAL0181 | SO | CSO on Sewer Network | SD7401104791 | GB112069061451 | Irwell (Croal to Irk) | SINGING CLOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 21.93 | 13 | 100%
United Utilities | STONELEIGH PARK CSO | STONELEIGH PARK CSO | 01OLD0039 | OLD0039 | SO | CSO on Sewer Network | SD9377006330 | GB112069064690 | Beal | RIVER BEAL VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 26.47 | 39 | 100%
United Utilities | STONETHWAITE WWTW | STONETHWAITE WwTW | 017570056 | 17570056 | ST | Storm Tank at WwTW | NY2594014160 | GB112075070340 | Stonethwaite Beck | TRIB STONETHWAITE BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 331.6 | 37 | 100%
United Utilities | STORE STREET | Store Street CSO | 016982994 | MAN0372 | SO | CSO on Sewer Network | SJ8486098010 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | STPETERS WAY/SPRINGFIELD IND ES CSO | St Peters Way/Springfield Industrial Estate CSO | 016982925 | BOL0208 | SO | CSO on Sewer Network | SD7228008811 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Commissioned in 2020 - full year data expected | 12.17 | 26 | 100%
United Utilities | STRAND ROAD STORM SEWER OVERFLOW | Trinity School / Strand Road Combined Sewer Overflow (Site ID 10015) xxxx ) (CAR0093) | 016931014 | CAR0093 | SO | CSO on Sewer Network | SJ3250094300 | 167 | #N/A | RIVER MERSEY | N/A | N/A | Commissioned in 2016 - full year data expected | 668.75 | 93 | 99.24% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | STRAND ROAD STORM SEWER OVERFLOW | Strand Road CSO | 016931014 | SEF0107 | SO | CSO on Sewer Network | SJ3250094300 | 167 | #N/A | RIVER MERSEY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 4.64 | 7 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | STRANGEWAY NO.1 WW NTWK PS | Strangeways No1 Ww Ntwk PS | 01WIG0097 | WIG0097 | SO | Storm Discharge at Pumping Station | SD6132003450 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | STRANGEWAY NO.2 WW NTWK PS | Strangeways PS No2 | 01WIG0096 | WIG0096 | SO | Storm Discharge at Pumping Station | SD6105003340 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | STRANGEWAYS CSO 50083 | Strangeways CSO | 016940235 | WIG0153 | SO | CSO on Sewer Network | SD6142003740 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 142 | 35 | 99.98%
United Utilities | STRETFORD RD/UPPER MOSS LN JUNC CSO | Stretford Road and Upper Moss Lane Junction CSO | 01MAN0365 | MAN0365 | SO | CSO on Sewer Network | SJ8252097362 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 23.07 | 7 | 89.32% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | STRETFORD WWTW | STRETFORD WwTW | 016940152 | 16940152 | ST | Storm Tank at WwTW | SJ7806093180 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2019 - full year data expected | 1230.88 | 91 | 99.93% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | STRINES STW | STRINES WwTW | 016940182 | 16940182 | ST | Storm Tank at WwTW | SJ9701187101 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Commissioned in 2019 - full year data expected | 870.41 | 109 | 86.65% | Sensor failure / issue | Resolved - December | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled
United Utilities | STRINES STW | STRINES WwTW | 016940182 | 16940182 | SO | Inlet CSO at WwTW | SJ9701187101 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Commissioned in 2019 - full year data expected | 578.36 | 31 | 96.4%
United Utilities | SUDDEN VALLEY SEWER | Sudden Valley SSO | 016981577 | ROC0156 | SO | CSO on Sewer Network | SD8819012280 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023 |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | SUDELL ROAD CSO | Sudell Road CSO | 017180464 | BBN0136 | SO | CSO on Sewer Network | SD6980022200 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 14.3 | 24 | 84.14% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | SUDELLSIDE STREET | Sudellside Street CSO | 017180466 | BBN0138 | SO | CSO on Sewer Network | SD6980022210 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | SUFFOLK ST COMBINED SEWER OVERFLOW | Suffolk Street CSO | 016983311 | OLD0037 | SO | CSO on Sewer Network | SD9084003810 | GB112069061120 | Wince Brook | BOWER BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 99.97%
United Utilities | SUNNY BANK ROAD CSO | Sunny bank Road CSO | 016993479 | BRY0067 | SO | CSO on Sewer Network | SD8082007390 | GB112069064600 | Roch (Spodden to Irwell) | PARR BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 126.17 | 75 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | SWALLOW HOUSE LANE CSO 212UB | Swallow House Lane Combined Sewer Overflow (Site ID 212UB) (PEA0057) | 01PEA0057 | PEA0057 | SO | CSO on Sewer Network | SK0308087350 | GB112069060970 | Sett | HOLLINGWORTH CLOUGH | n/a | n/a | Commissioned in 2017 - full year data expected | 146.77 | 66 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | SWAN LANE HINDLEY CSO 503J8 | Swan Lane Hindley CSO | 016920473 | WIG0150 | SO | CSO on Sewer Network | SD6424003810 | GB112069060820 | Westleigh Brook | MARSH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 47.13 | 39 | 100%
United Utilities | SWAN MILL/DRUMMER MILL CSO | Swan Mill CSO | 016983314 | OLD0042 | SO | CSO on Sewer Network | SD8896004570 | GB112069061120 | Wince Brook | SPRINGS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 336.02 | 99 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | TALKE INDUSTRIAL EST CSO | Talke Industrial Estate Combined Sewer Overflow (Site ID 292UG) (NEW0037) | 016881957 | NEW0037 | SO | CSO on Sewer Network | SJ8205052251 | GB112068074630 | Valley Brook (Source to Englesea Brook) | TRIB VALLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | TALKIN WWTW | TALKIN WwTW | 017670095 | 17670095 | ST | Storm Tank at WwTW | NY5475057700 | GB102076074040 | Gelt | WILLY BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 130.02 | 54 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TALLENTIRE PUMPING STATION | Tallentire (West) PS | 017570058 | ALL0092 | SO | Storm Discharge at Pumping Station | NY1003235482 | GB112075073570 | Broughton Beck | UNNAMED TRIB OF BROUGHTON BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 683.06 | 72 | 99.84% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | TAME STREET/PARK ROAD CSO | Tame Street/Park Road CSO | 01TAM0109 | TAM0109 | SO | CSO on Sewer Network | SJ9539098160 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | TANHOUSE LANE | Tan House Lane/ Moss Bank Road CSO | 01HAL0052 | HAL0052 | SO | CSO on Sewer Network | SJ5274084830 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | TANPITS ROAD CSO | Tanpits Road | 016982617 | BRY0098 | SO | CSO on Sewer Network | SD7973010660 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | n/a | n/a | Commissioned in 2018 - full year data expected | 238.47 | 58 | 93.81% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TARPORLEY WWTW | TARPORLEY WwTW | 016810110 | 16810110 | ST | Storm Tank at WwTW | SJ5633061240 | GB112068055440 | Wettenhall Brook | WETTENHALL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 1003.11 | 126 | 99.24% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation
United Utilities | TARPORLEY WWTW | TARPORLEY WwTW | 016810110 | 16810110 | SO | Inlet CSO at WwTW | SJ5633061240 | GB112068055440 | Wettenhall Brook | WETTENHALL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 97.29 | 39 | 100%
United Utilities | TARVIN STW | TARVIN WwTW | 016810035 | 16810035 | SO | Inlet CSO at WwTW | SJ4890067500 | GB112068060290 | Milton Brook | MILTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | TEBAY PUMPING STATION | Tebay Sewage PS | 017280240 | EDE0079 | SO | Storm Discharge at Pumping Station | NY6155005240 | GB112072071760 | Lune - headwaters to conf Birk Beck | RIVER LUNE | N/A | N/A | Commissioned in 2018 - full year data expected | 766.9 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | TEBAY STW | TEBAY WwTW | 017270018 | 17270018 | SO | Inlet CSO at WwTW | NY6135202882 | GB112072071720 | Lune - conf Birk Beck to conf Rawthey | RIVER LUNE | N/A | N/A | Commissioned in 2020 - full year data expected | 1459.34 | 159 | 100% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | TEMPLE SOWERBY WWTW | TEMPLE SOWERBY WwTW | 017670042 | 17670042 | SO | Inlet CSO at WwTW | NY6106027880 | GB102076070950 | Crowdundle Beck - Lower | BIRK SYKE | N/A | N/A | Commissioned in 2019 - full year data expected | 2258.88 | 237 | 99.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TEMPLETON ROAD WW NETWORK PS | Templeton Road PS | 01WIG0095 | WIG0095 | SO | Storm Discharge at Pumping Station | SD6050002450 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Commissioned in 2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | THE AVENUE (CHURCHTOWN) CSO | The Avenue (churchtown) CSO | 017290551 | WYR0081 | SO | CSO on Sewer Network | SD4877042970 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | N/A | Commissioned in 2020 - full year data expected | 104.9 | 15 | 100%
United Utilities | THE AVENUE SYPHON CSO 452UO | The Avenue Syphon CSO | 016982888 | TRA0096 | SO | CSO on Sewer Network | SJ7645092842 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BRK TRIB RVR MERSEY | n/a | n/a | Commissioned in 2018 - full year data expected | 105.43 | 63 | 97.42% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THE BROW CSO 202UP | The Brow CSO | 016892107 | HAL0055 | SO | CSO on Sewer Network | SJ5315083440 | 169 | #N/A | MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2017 - full year data expected | 9.93 | 12 | 100%
United Utilities | THE BURROUGHS CSO 022UQ | The Burroughs CSO | 01ALL0023 | ALL0023 | SO | CSO on Sewer Network | NY1091031050 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | n/a | n/a | Commissioned in 2018 - full year data expected | 103.47 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THE BYPASS/LPOOL RD JUNCT CSO 382UR | The Bypass / Liverpool Road Junction CSO | 016982752 | SEF0099 | SO | CSO on Sewer Network | SJ3050098906 | 348 | #N/A | RIVER MERSEY ESTUARY | n/a | n/a | Commissioned in 2017 - full year data expected | 5.87 | 21 | 81.2% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | THE CARRS COMBINED SEWER OVERFLOW | THE CARRS CSO | 01MAC0044 | MAC0044 | SO | CSO on Sewer Network | SJ8420081700 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Commissioned in 2018 - full year data expected | 178.37 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THE CAUSEWAY CHADDERTON WWNPS | The Causeway (Chadderton) Wastewater Network Pumping Station | 016983315 | OLD0121 | SO | Storm Discharge at Pumping Station | SD8910004470 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | N/A - Ongoing investigation |  | Investigation now complete, remedial work due
United Utilities | THE CIRCUIT CSO 432UT | The Circuit CSO | 016982668 | STK0103 | SO | CSO on Sewer Network | SJ8748089890 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 66.03 | 32 | 67.08% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | THE CRESCENT CSO 091EJ | The Crescent CSO | 01BRY0043 | BRY0043 | SO | CSO on Sewer Network | SD8174003690 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH VIA SWS | N/A | N/A | Commissioned in 2018 - full year data expected | 0.6 | 4 | 81.82% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | THE CSO AT MAIN STREET | The CSO at Main Street | 017580276 | ALL0129 | SO | CSO on Sewer Network | NY0711628810 | GB112075070540 | Marron | TOWNSEND BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.27 | 2 | 99.73%
United Utilities | THE DELL COMBINED SEWER OVERFLOW | The Dell CSO | 016881648 | WIR0139 | SO | CSO on Sewer Network | SJ3417086368 | 171 | #N/A | THE MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 267.41 | 110 | 99.48% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | THE FLATS CSO 171U1 | The Flats CSO | 017680350 | EDE0107 | SO | CSO on Sewer Network | NY5074046100 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | n/a | n/a | Commissioned in 2017 - full year data expected | 1.2 | 7 | 100%
United Utilities | THE GLEN COMBINED SEWER OVERFLOW | The Glen CSO | 016993608 | ROS0030 | SO | CSO on Sewer Network | SD8409021650 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 1190.18 | 151 | 98.22% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | THE GRANGE CONGLETON CSO | The Grange (Congleton) Combined Sewer Overflow (Site ID 132UW) (CON0032) | 01CON0032 | CON0032 | SO | CSO on Sewer Network | SJ8604063240 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 76.8 | 50 | 99.53% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THE GREENACRES CSO | The Greenacres CSO | 017180545 | SRI0060 | SO | CSO on Sewer Network | SD4979027051 | 175 | #N/A | UNNAMED TRIB. OF MILL BROOK | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 33.37 | 14 | 100%
United Utilities | THE OLD VICARAGE CSO | The Old Vicarage CSO | 016981472 | PEA0068 | SO | CSO on Sewer Network | SK0107080790 | GB112069060860 | Randall Carr Brook | RANDALL CARR BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | THERMAL ROAD/PORT CAUSEWAY CSO | Dock Road South | 016881611 | WIR0134 | SO | CSO on Sewer Network | SJ3580083650 | GB531206908100 | MERSEY | THE MERSEY ESTUARY | N/A | N/A | Commissioned in 2016 - full year data expected | 769.83 | 100 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THERMAL ROAD/PORT CAUSEWAY CSO | Thermal Road Port, Causeway | 016881611 | WIR0132 | SO | CSO on Sewer Network | SJ3580083650 | GB531206908100 | MERSEY | THE MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 36.87 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THEWLIS STREET CSO | Thewlis Street CSO | 01WAR0060 | WAR0060 | SO | CSO on Sewer Network | SJ5950087910 | 170 | #N/A | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | THICK RIGGS CSO (022UY) | THICK RIGGS CSO | 01ALL0024 | ALL0024 | SO | CSO on Sewer Network | NY2508023860 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER DERWENT | N/A | N/A | Commissioned in 2018 - full year data expected | 21 | 4 | 100%
United Utilities | THICKETFORD CSO 072UX | Thicketford CSO | 016982835 | BOL0229 | SO | CSO on Sewer Network | SD7357010430 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 97.73 | 37 | 100%
United Utilities | THOMPSON ROAD CSO | Thompson Road Combined Sewer Overflow (Site ID 07055) (BOL0053) | 016950279 | BOL0053 | SO | CSO on Sewer Network | SD6993010450 | GB112069064540 | Middle Brook | CAPTAINS CLOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 860.36 | 113 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | THORNCLIFFE RD/CLIFF LN CSO | Thorncliff Road/Cliff Lane CSO | 017480405 | BRW0033 | SO | CSO on Sewer Network | SD2194069340 | GB112074069790 | Mill Beck (Poaka Beck) | MILL BECK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | THORNLEY LANE SOUTH CSO 44019 | Thornley Lane South CSO | 016993676 | TAM0065 | SO | CSO on Sewer Network | SJ9038094300 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | UNNAMED TRIB DENTON BRK SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 33.4 | 24 | 100%
United Utilities | THORNPARK PUMPING STATION 33007 | THORNPARK PS | 01PRE0082 | PRE0082 | SO | CSO on Sewer Network | SD4983029960 | 176 | #N/A | UNNAMED TRIB OF RVR RIBBLE | RIBBLE | St Annes | Commissioned in 2016 - full year data expected | 115.51 | 33 | 100%
United Utilities | THORNTON HOUGH PUMPING STATION | Thornton Hough PS | 016892274 | WIR0149 | SO | Storm Discharge at Pumping Station | SJ3071080550 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | THORNTON HOUGH,TRIB OF CLATTER | n/a | n/a | Commissioned in 2017 - full year data expected | 39.77 | 51 | 99.73% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THORNTON HOUGH PUMPING STATION | Thornton PS | 016892274 | SEF0115 | SO | Storm Discharge at Pumping Station | SJ3071080550 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | THORNTON HOUGH,TRIB OF CLATTER | N/A | Formby | Commissioned in 2017 - full year data expected | 120.22 | 49 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THORNTON ROAD DEPOT CSO 482U7 | Thornton Road Depot CSO | 01WAR0013 | WAR0013 | SO | CSO on Sewer Network | SJ5776087340 | 170 | #N/A | SANKEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 135.53 | 60 | 96.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THORNTON ROAD ELLESMERE PORT CSO | Little Stanney SO | 016881595 | ELL0033 | SO | CSO on Sewer Network | SJ4155074980 | GB112068060260 | Stanney Mill Brook | STANNEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 96.9 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THREAPLAND WWTS | Threapland WwTW | 017570074 | 17570074 | ST | Storm Tank at WwTW | NY1555039470 | GB112075073620 | Threapland Gill | THREAPLAND GILL | n/a | n/a | Commissioned in 2018 - full year data expected | 283.03 | 62 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | THRELKELD PS | Threlkeld Quarry PS | 017580261 | ALL0110 | SO | Storm Discharge at Pumping Station | NY3169024680 | GB112075070460 | Glenderamackin (Greta) | RIVER GLENDERAMACKIN | N/A | N/A | Commissioned in 2020 - full year data expected | 432.77 | 77 | 99.78% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | THURLWOOD NO.1 PS | Thurlwood No 1 PS | 016881933 | CON0067 | SO | Storm Discharge at Pumping Station | SJ8005057690 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | TRENT AND MERSEY CANAL | N/A | N/A | Commissioned in 2019 - full year data expected | 89.16 | 29 | 100%
United Utilities | THURSBY STW | THURSBY WwTW | 017570018 | 17570018 | SO | Inlet CSO at WwTW | NY3173050340 | GB102075073410 | Wampool (Upper) | MATTY BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 447.34 | 86 | 99.99% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation
United Utilities | THURTELL COTTAGES CSO LAN0091 | Thurtell Cottages CSO | 01LAN0091 | LAN0091 | SO | CSO on Sewer Network | SD5280065240 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Commissioned in 2016 - full year data expected | 73.33 | 36 | 99.99% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | THWAITES BREWERY YARD | Thwaites Brewery Yard CSO | 01BBN0030 | BBN0030 | SO | CSO on Sewer Network | SD6843028330 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 181.7 | 59 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | TIMBER STREET CSO 32021 | Timber Street CSO | 01PEN0022 | PEN0022 | SO | CSO on Sewer Network | SD8466036720 | GB112071065490 | Calder - Pendle Water to conf Ribble | UNNAMED TRIB OF PENDLE WATER | n/a | n/a | Commissioned in 2018 - full year data expected | 49.57 | 54 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TINKER BROOK CSO (22018) | Tinker Brook CSO | 017160120 | HYN0006 | SO | CSO on Sewer Network | SD7416028380 | GB112071065050 | Hyndburn Brook - Upper | TINKER BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 27.96 | 31 | 99.99%
United Utilities | TINTERN ROAD (OFF THE LAND) CSO | Tintern Road (Off the Land) CSO | EPRQB3594AD | ROC0134 | SO | CSO on Sewer Network | SD8733007390 | GB112069061161 | Irk (Sourtce to Wince Brook) | TRIB OF TRUB BROOK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0.5 | 7 | 100%
United Utilities | TINTWISTLE STW | TINTWISTLE WwTW | 016940183 | 16940183 | ST | Storm Tank at WwTW | SK0176096770 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation
United Utilities | TOAD LANE - HIGH STREET CSO | Toad Lane - High Street CSO | 016950161 | ROC0140 | SO | CSO on Sewer Network | SD8928013340 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 3.03 | 10 | 100%
United Utilities | TONG LANE/REED STREET CSO | TONG LANE / REED STREET CSO | 01ROS0019 | ROS0019 | SO | CSO on Sewer Network | SD8710023170 | GB112069064660 | Irwell (Source to Whitewell Brook) | GLEAVE CLOUGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | TONGE MOOR RD CSO | Tonge Moor Road CSO | 016982274 | BOL0200 | SO | CSO on Sewer Network | SD7256010000 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | TONGE VALLEY CSO | Tonge Valley CSO | 016983223 | BOL0084 | SO | CSO on Sewer Network | SD7208010910 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Commissioned in 2020 - full year data expected | 0.17 | 1 | 100%
United Utilities | TORKINGTON ROAD CSO | Torkington Road CSO | 016982664 | STK0098 | SO | CSO on Sewer Network | SJ9338087070 | GB112069060950 | Poise Brook | TRIB OF OCHERLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0.5 | 1 | 100%
United Utilities | TORPENHOW WWTW (TORPE) | TORPENHOW WwTW | 017570075 | 17570075 | SO | Inlet CSO at WwTW | NY2075040410 | GB112075073600 | Cockshot Beck | COCKSHOT BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 559.35 | 103 | 99.99% |  |  | Performance - Infiltration | N/A - Ongoing investigation
United Utilities | TORRS DIVERSION CSO 21123 | Torrs Diversion Sewer CSO | 01PEA0023 | PEA0023 | SO | CSO on Sewer Network | SK0011085271 | GB112069060970 | Sett | RIVER GOYT VIS SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 632.07 | 109 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | TORVER STW | TORVER WwTW | 017370039 | 17370039 | SO | Inlet CSO at WwTW | SD2817093930 | GB112073071200 | Torver Beck | TORVER BECK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | TOWN BECK CSO 39065 | Town Beck CSO | 017380295 | LAK0059 | SO | CSO on Sewer Network | SD2918078120 | GB112073071160 | Dragley Beck | TOWN BECK | Morecambe Bay (Leven) | n/a | Commissioned in 2017 - full year data expected | 20.22 | 15 | 100%
United Utilities | TOWN LANE CIRCULAR ROAD CSO 44020 | Town Lane/Circular Road CSO | 01TAM0067 | TAM0067 | SO | CSO on Sewer Network | SJ9192094851 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK TRIB RIVER TAME | n/a | n/a | Commissioned in 2018 - full year data expected | 180.41 | 72 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | TOWN LANE CSO | Town Lane CSO | 016881767 | MAC0162 | SO | CSO on Sewer Network | SJ7891079820 | GB112069061330 | Mobberley Brook | MOBBERLEY BROOK TRIB RV BOLLIN | n/a | n/a | Commissioned in 2018 - full year data expected | 951.63 | 146 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TOWN PUMPING STATION | Town PS | 016881718 | ELL0035 | SO | Storm Discharge at Pumping Station | SJ4095077100 | 171 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2019 - full year data expected | 331.34 | 85 | 99.93% |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation
United Utilities | TOWN STREET COMBINED SEWER OVERFLOW | Town Street Combined Sewer Overflow (Site ID 439AB) (STK0138) | 016982519 | STK0138 | SO | CSO on Sewer Network | SJ9649089440 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Commissioned in 2016 - full year data expected | 342.06 | 49 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TOWNGATE/FOX LANE CSO | Towngate/ Fox Lane CSO | 017081318 | SRI0016 | SO | CSO on Sewer Network | SD5401021320 | GB112070064912 | Lostock DS Farington Weir | CRICKETFIELD BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 0.27 | 2 | 100%
United Utilities | TOWNSGATE COMBINED SEWER OVERFLOW | TOWNSGATE CSO | 01TRA0037 | TRA0037 | SO | CSO on Sewer Network | SJ7288094050 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 928.17 | 121 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TRAFALGAR STREET /RAMSEY STREET CSO | Trafalgar Street/Ramsey Street Combined Sewer Overflow | NPSWQD010102 | ROC0071 | SO | CSO on Sewer Network | SD9045013510 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 36.81% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | TRAFFORD PARK ROAD CSO | Trafford Park Road CSO | 016940329 | TRA0070 | SO | CSO on Sewer Network | SJ7977097430 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 12.97 | 9 | 100%
United Utilities | TRAVIS BROW/GEORGES ROAD CSO | Hope Street CSO | 016982677 | STK0107 | SO | CSO on Sewer Network | SJ8860090210 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2016 - full year data expected | 427.97 | 105 | 99.77% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | TRAVIS BROW/GEORGES ROAD CSO | Travis Brow/Georges Road CSO | 016982677 | STK0115 | SO | CSO on Sewer Network | SJ8860090210 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2016 - full year data expected | 89 | 56 | 99.44% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | TRENTHAM P.S | Trentham Street PS | 016820392 | HAL0029 | SO | Storm Discharge at Pumping Station | SJ5070083441 | 169 | #N/A | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | TRINITY ST/DEAN ST | Trinity Street/Dean Street CSO | 016993730 | TAM0103 | SO | CSO on Sewer Network | SJ9636098530 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | THE RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 0.53 | 7 | 100%
United Utilities | TROUTBECK ROAD CSO 508B3 | Troutbeck Road CSO | 016983357 | WIG0105 | SO | CSO on Sewer Network | SJ5455098970 | GB112069061230 | Black Brook (Mersey Estuary) | MILLINGFORD BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.43 | 1 | 100%
United Utilities | TRUNNAH ROAD PUMPING STATION | Trunnah Road PS | 017290503 | WYR0017 | SO | Storm Discharge at Pumping Station | SD3386043240 | GB112072066160 | Hillylaid Pool - Main Dyke | ROYALS BROOK | N/A | N/A | Commissioned in 2016 - full year data expected | 52.6 | 8 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | TURNER BRIDGE CSO | Turner Bridge CSO | 016983218 | BOL0092 | SO | CSO on Sewer Network | SD7251009960 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Commissioned in 2019 - full year data expected | 239.02 | 92 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | TURNER LANE/ALEXANDRA ROAD | Turner Lane/Alexandra Road CSO | 016993751 | TAM0042 | SO | CSO on Sewer Network | SJ9394098770 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | THE RIVER TAME | N/A | N/A | Commissioned in 2019 - full year data expected | 407.15 | 98 | 55.37% | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | TURPIN GREEN LANE CSO | Turpin Green Lane CSO | 017081364 | SRI0020 | SO | CSO on Sewer Network | SD5456022510 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 12.8 | 25 | 100%
United Utilities | TWIST LANE/WESTLEIGH BRIDGE CSO | Twist Lane/Westleigh Bridge CSO | 01WIG0065 | WIG0065 | SO | CSO on Sewer Network | SD6482000241 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 19.17 | 11 | 100%
United Utilities | TYLDESLEY STW | TYLDESLEY WwTW | 016920135 | 16920135 | ST | Storm Tank at WwTW | SJ6959099000 | GB112069061100 | Astley Brook (Mersey) | MOSS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1612.33 | 117 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TYLDESLEY STW | Tyldesley Western CSO | 016920135 | WIG0151 | SO | CSO on Sewer Network | SJ6959099000 | GB112069061100 | Astley Brook (Mersey) | MOSS BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 371.6 | 54 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | TYNESBANK | Tynesbank CSO | 01SAL0062 | SAL0062 | SO | CSO on Sewer Network | SD7338002780 | GB112069061090 | Shaw Brook | ELLEN BROOK CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 165.12 | 52 | 48.6% | Sensor failure / issue | Resolved - September | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | ULLGILL MORESBY (MH65) CSO | Ullgill Moresby (MH65) CSO | 017580419 | COP0066 | SO | CSO on Sewer Network | NX9903021260 | GB112074070040 | Lowca Beck | TRIB OF LOWCA BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 6.43 | 5 | 100%
United Utilities | ULVERSTON WWTW | ULVERSTON WwTW | 017370179 | 17370179 | SO | Inlet CSO at WwTW | SD3071077240 | GB112073071160 | Dragley Beck | ULVERSTON CHANNEL/ CARTER POOL | N/A | N/A | Commissioned in 2017 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | UNTHANK PUMPING STATION | Unthank PS | 017680386 | EDE0111 | SO | Storm Discharge at Pumping Station | NY6092040390 | GB102076073820 | Glassonby Beck | HAZELRIGG BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 105.13 | 24 | 97.88%
United Utilities | UPTON ROAD CSO 513N8 | Upton Road CSO | 01WIR0004 | WIR0004 | SO | CSO on Sewer Network | SJ2761089731 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | n/a | n/a | Commissioned in 2017 - full year data expected | 45.3 | 36 | 100%
United Utilities | UPTON STORM TANKS | Upton Storm Tanks | 01WIR0071 | WIR0071 | SO | CSO on Sewer Network | SJ2769089030 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | North Wirral East | Wallasey | Commissioned in 2016 - full year data expected | 371.12 | 47 | 99.54% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | URMSTON SSO | Richmond Road CSO | 016941193 | TRA0003 | SO | CSO on Sewer Network | SJ7786097992 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | URMSTON WASTEWATER TREATMENT WORKS | URMSTON WwTW | 016940154 | 16940154 | ST | Storm Tank at WwTW | SJ7287093990 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | n/a | n/a | Commissioned in 2018 - full year data expected | 3101.65 | 189 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | VALE STREET | Vale Street | 017180471 | BBN0146 | SO | CSO on Sewer Network | SD6884022540 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | VALLETS LANE CSO | Vallets Lane Combined Sewer Overflow (07046) (BOL0227) | 016982920 | BOL0227 | SO | CSO on Sewer Network | SD7015010340 | GB112069064540 | Middle Brook | CLVRT OF CAPTAINS CLOUGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 518.31 | 40 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Ongoing investigation
United Utilities | VALLEY DRIVE CSO | Rear of Valley Drive CSO | 01ELL0008 | ELL0008 | SO | CSO on Sewer Network | SJ3795076560 | GB112068060350 | Rivacre Brook | RIVACRE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 11.8 | 5 | 99.99%
United Utilities | VALLEY ROAD PUMPING STATION | Valley Road PS | 017160300 | SRI0003 | SO | Storm Discharge at Pumping Station | SD5281028450 | 175 | #N/A | RIVER RIBBLE | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 70.68 | 24 | 99.76%
United Utilities | VAUGHAN STREET CSO | Bennett Street CSO | 016982957 | MAN0376 | SO | CSO on Sewer Network | SJ8688097060 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CLVRT SECTION OF CORN BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 302.23 | 24 | 89.63%
United Utilities | VAUGHAN STREET CSO | Vaughan Street Combined Sewer Overflow | 016993693 | MAN0218 | SO | CSO on Sewer Network | SJ8688097060 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CORN BROOK IN CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 0.17 | 2 | 100%
United Utilities | VERDON STREET/SCOTLAND CSO | Verdon Street/Scotland Combined Sewer Overflow | 016982715 | MAN0265 | SO | CSO on Sewer Network | SJ8412099170 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 20.23 | 2 | 100%
United Utilities | VICARAGE LANE CSO 022WD | Vicarage Lane | 017580253 | ALL0097 | SO | CSO on Sewer Network | NY1275030230 | GB112075070390 | Tom Rudd Beck | TOM RUDD BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | VICARAGE ROAD | Vicarage Road CSO | 01STH0079 | STH0079 | SO | CSO on Sewer Network | SJ5429097180 | GB112069061230 | Black Brook (Mersey Estuary) | 0 | n/a | n/a | Commissioned in 2018 - full year data expected | 23.37 | 6 | 100%
United Utilities | VICARAGE ROAD CSO | Vicarage Road CSO | 016881768 | CRE0075 | SO | CSO on Sewer Network | SJ6612043510 | GB112068055190 | Audlem Brook | SWANBACK MILL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 76.57 | 31 | 100%
United Utilities | VICARS HALL LANE PS NO 2 | Vicars Hall Lane PS No. 1 & CSO | 016983333 | SAL0002 | SO | CSO on Sewer Network | SD7170100361 | GB112069061090 | Shaw Brook | ELLEN BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 407.07 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | VICTORIA AVENUE/GLENBROOK CSO | Victoria Avenue/Glenbrook CSO | 016993670 | MAN0093 | SO | CSO on Sewer Network | SD8404004060 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | VICTORIA AVENUE/RIVER IRK CSO | VICTORIA AVENUE/RIVER IRK CSO | 01MAN0094 | MAN0094 | SO | CSO on Sewer Network | SD8404004050 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Commissioned in 2019 - full year data expected | 9.67 | 10 | 100%
United Utilities | VICTORIA BRIDGE STREET CSO (282WL) | Victoria Bridge Street CSO | 01MAN0155 | MAN0155 | SO | CSO on Sewer Network | SJ8377098690 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 66.33 | 33 | 99.99% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | VICTORIA RD/ORVIETTO AVENUE CSO | Victoria Road CSO | 016993481 | PRE0119 | SO | CSO on Sewer Network | SJ7844099750 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK VIA SWS | n/a | n/a | Commissioned in 2018 - full year data expected | 269.29 | 69 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | VICTORIA RD/ORVIETTO AVENUE CSO | Victoria Road/Orvietto Avenue CSO | 016993481 | SAL0078 | SO | CSO on Sewer Network | SJ7844099750 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK VIA SWS | N/A | N/A | Commissioned in 2018 - full year data expected | 0.43 | 2 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | VICTORIA ST CSO 212WG | Victoria Street CSO | 01PEA0034 | PEA0034 | SO | CSO on Sewer Network | SK0346093940 | GB112071065310 | Blakewater | RIVER BLAKEWATER | n/a | n/a | Commissioned in 2020 - full year data expected | 0.2 | 2 | 100% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | VICTORIA ST/ACRE ST CSO (442WA) | Victoria Street/Acre Street Storm Overflow | 01TAM0062 | TAM0062 | SO | CSO on Sewer Network | SJ9169094650 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA SWS | N/A | N/A | Commissioned in 2020 - full year data expected | 40.73 | 38 | 100%
United Utilities | VICTORIA STREET CSO | VICTORIA STREET CSO | 01BBN0047 | BBN0047 | SO | CSO on Sewer Network | SD6840028400 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 6.07 | 45 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WADDINGTON WWTW | WADDINGTON WwTW | 017160048 | 17160048 | ST | Storm Tank at WwTW | SD7230043050 | GB112071065520 | Bashall Brook | BASHALL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 3814.62 | 186 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WAGGON ROAD CSO | WAGGON ROAD CSO | 01TAM0091 | TAM0091 | SO | CSO on Sewer Network | SD9753001970 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Commissioned in 2018 - full year data expected | 0.9 | 7 | 100% |  |  |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WAKELING RD/STOCKPORT RD | Wakeling/Stockport Road CSO | 01TAM0070 | TAM0070 | SO | CSO on Sewer Network | SJ9223093880 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIBUTARY OF RIVER TAME | N/A | N/A | Commissioned in 2020 - full year data expected | 7.4 | 14 | 100%
United Utilities | WALKDEN RD HOLYOAKE RD CSO 37045 | Walkden Road/Hoylake Road CSO | 016983330 | SAL0113 | SO | CSO on Sewer Network | SD7384002760 | GB112069061430 | Folly Brook and Salteye Brook. | WORSLEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 161.27 | 49 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WALLACRE ROAD CSO | Wallacre Road CSO | 016892470 | WIR0151 | SO | CSO on Sewer Network | SJ2914091650 | GB112068060530 | The Birket including Arrowe Brook and Fender | MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 64.8 | 43 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WALLACRE ROAD/BEAUFORT DRIVE CSO | Wallacre Road/Beaufort Drive CSO | 016892477 | WIR0061 | SO | CSO on Sewer Network | SJ2916091660 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 2.13 | 4 | 100%
United Utilities | WALLASEY COASTAL DRIVE 51052 | Wallasey Detention Tank | 016983123 | WIR0145 | SO | Storm Discharge at Pumping Station | SJ2945094053 | 351 | #N/A | RIVER MERSEY ESTUARY | North Wirrall (East) and North Wirrall (West) | Meols, Moreton and Wallasey | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | WALLASEY WW PUMPING STATION | Wallasey PS | 016983300 | WIR0146 | SO | Storm Discharge at Pumping Station | SJ3262090640 | 171 | #N/A | RIVER MERSEY ESTUARY | N/A | N/A | Commissioned in 2018 - full year data expected | 1271.27 | 197 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WALLASEY WW PUMPING STATION | Wallasey PS | 016983300 | WIR0146 | SO | Storm Discharge at Pumping Station | SJ3262090640 | 171 | #N/A | RIVER MERSEY ESTUARY | N/A | N/A | Commissioned in 2018 - full year data expected | 202.48 | 62 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WALLASEY WW PUMPING STATION | Wallasey PS | 016983300 | WIR0146 | SO | Storm Discharge at Pumping Station | SJ3262090640 | 171 | #N/A | RIVER MERSEY ESTUARY | N/A | N/A | Commissioned in 2018 - full year data expected | 11.44 | 6 | 100%
United Utilities | WALTON PS | WALTON PUMPING STATION | 016920316 | WAR0022 | SO | Storm Discharge at Pumping Station | SJ6029086070 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2019 - full year data expected | 446.95 | 56 | 99.99% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | WALTON-LE-DALE STW | WALTON-LE-DALE WwTW | 017160065 | 17160065 | ST | Storm Tank at WwTW | SD5460028200 | 175 | #N/A | RIVER RIBBLE ESTUARY | N/A | N/A | Commissioned in 2020 - full year data expected | 521.36 | 47 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WALVERDEN PARK CSO | Walverden Park CSO | 017180618 | PEN0082 | SO | CSO on Sewer Network | SD8648037530 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Commissioned in 2019 - full year data expected | 8.85 | 18 | 99.92%
United Utilities | WALWYN CLOSE CSO 45049 | Walwyn Close CSO | 01TRA0056 | TRA0056 | SO | CSO on Sewer Network | SJ8009093550 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 502.94 | 81 | 98.04% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WARDLE BRIDGE PUMPING STATION | Wardle Bridge PS | 016892468 | CON0006 | SO | Storm Discharge at Pumping Station | SJ7067066120 | GB112068055460 | Croco | THE RIVER CROCO | n/a | n/a | Commissioned in 2017 - full year data expected | 158.18 | 58 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WARGRAVE ROAD CSO | Wargrave Road CSO | NPSWQD004566 | STH0123 | SO | CSO on Sewer Network | SJ5901194760 | GB112069061220 | Millingford (Newton) Brook | NEWTON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WARICK ROADWWNW PS | Warwick Road WwNPS | 017680359 | CAR0071 | SO | Storm Discharge at Pumping Station | NY4180056080 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Commissioned in 2019 - full year data expected | 4.22 | 13 | 99.96%
United Utilities | WARRINGTON NEW ROAD CSO | Warrington New Road CSO | 01STH0052 | STH0052 | SO | CSO on Sewer Network | SJ5195095050 | GB112069061210 | Hardshaw (Windle) Brook | HARDSHAW BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WARRINGTON NEW ROAD (42060) | Warrington New Road CSO | 016993695 | STH0050 | SO | CSO on Sewer Network | SJ5187095180 | GB112069061210 | Hardshaw (Windle) Brook | HARDSHAW BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 51.61 | 30 | 99.98%
United Utilities | WARRINGTON NORTH WWTW | WARRINGTON NORTH WwTW | 016983122 | 16983122 | ST | Storm Tank at WwTW | SJ5804086890 | 170 | #N/A | MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 1507.31 | 126 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WARRINGTON NORTH WWTW | WARRINGTON NORTH WwTW | 016983122 | 16983122 | SO | Inlet CSO at WwTW | SJ5804086890 | 170 | #N/A | MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 135.05 | 42 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WARRINGTON RD/WITHINGTON | Warrington Road/Withington Avenue | 01WAR0109 | WAR0109 | SO | CSO on Sewer Network | SJ6608095240 | GB112069061420 | Glaze | 0 | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WARRINGTON ROAD CSO | WARRINGTON ROAD CSO | 01HAL0054 | HAL0054 | SO | CSO on Sewer Network | SJ5205084650 | 170 | #N/A | BOWERS BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 143.2 | 63 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WARRINGTON ROAD CSO | Warrington Road CSO | NPSWQD001822 | WIG0247 | SO | CSO on Sewer Network | SJ6681098480 | 170 | #N/A | BOWERS BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 17.89 | 8 | 99.93%
United Utilities | WARRINGTON ROAD PS | Warrington Road (Risley) PS | 01WAR0031 | WAR0031 | SO | Storm Discharge at Pumping Station | SJ6392092540 | GB112069061020 | Spittle Brook | UNNAMED TRIBUTARY CROSS BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 176.34 | 40 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WARRINGTON ROAD WA5 2JL CSO | The Warrington Road CSO | 016993441 | WAR0080 | SO | CSO on Sewer Network | SJ5727087730 | GB112069060990 | Whittle Brook (Mersey Estuary) | WHITTLE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 23.35 | 23 | 99.88%
United Utilities | WARRINGTON SOUTH WWTW | WARRINGTON SOUTH WwTW | 016820128 | 16820128 | ST | Storm Tank at WwTW | SJ5870085580 | 169 | #N/A | M/C SHIP CANAL (TIDAL) | N/A | N/A | Commissioned in 2019 - full year data expected | 3399.47 | 163 | 100% |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - November
United Utilities | WARRINGTON/GRAPPENHALL | Grappenhall Resewerage Scheme | 016921094 | WAR0025 | SO | CSO on Sewer Network | SJ6295087000 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WARWICK BRIDGE PS | Warwick Bridge PS | 017680331 | CAR0086 | SO | Storm Discharge at Pumping Station | NY4737056940 | GB102076073900 | Trout Beck (Cairn Beck) | CAIRN BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 27.26 | 20 | 100%
United Utilities | WARWICK ON EDEN PS | Warwick on Eden PS | 017680330 | CAR0085 | SO | Storm Discharge at Pumping Station | NY4696056660 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WASHWAY LANE | Washway Lane CSO | 016920387 | STH0058 | SO | CSO on Sewer Network | SJ5134097130 | GB112069061240 | Rainford Brook | RAINFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 106.32 | 59 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WASTDALE DRIVE CSO | Wastdale Drive CSO | 016892255 | WIR0074 | SO | CSO on Sewer Network | SJ2492090200 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | NORTH WIRRAL (WEST) | Moreton | Commissioned in 2016 - full year data expected | 207.76 | 53 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WASTE LANE CSO SITE ID 472W0 | WASTE LANE CSO | 01VRY0055 | VRY0055 | SO | CSO on Sewer Network | SJ5944071600 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 11.87 | 14 | 95.29%
United Utilities | WATER ST/NEW QUAY ST CSO | Water Street/New Quay Street CSO | 016993831 | MAN0172 | SO | CSO on Sewer Network | SJ8312098220 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | THE RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 36.81% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | WATER STREET CSO | Water Street CSO | EPRSB3793VY | MAC0056 | SO | CSO on Sewer Network | SJ9351677848 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Commissioned in 2018 - full year data expected | 39.3 | 38 | 99.99%
United Utilities | WATER STREET CSO | Water Street | EPRQB3593RF | ROC0097 | SO | CSO on Sewer Network | SD9006013400 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 27.33 | 23 | 100%
United Utilities | WATER STREET CSO (284TV) | Water Street (Manchester) CSO | 016982993 | MAN0391 | SO | CSO on Sewer Network | SJ8295098030 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WATER STREET CSO 07020 | Water Street CSO | 016982191 | BOL0171 | SO | CSO on Sewer Network | SD7205009500 | GB112069064540 | Middle Brook | RIVER CROAL | n/a | n/a | Commissioned in 2018 - full year data expected | 0.95 | 1 | 100%
United Utilities | WATER STREET/LIVERPOOL ROAD CSO | Water Street/Liverpool Road CSO | 016993597 | MAN0169 | SO | CSO on Sewer Network | SJ8282297894 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 47.9 | 19 | 99.61%
United Utilities | WATERBARN LANE CSO | WATERBARN LANE CSO | 01ROS0018 | ROS0018 | SO | CSO on Sewer Network | SD8450021710 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 9.8 | 5 | 100%
United Utilities | WATERBARN LANE CSO | Waterbarn Street/Barden Lane Combined Sewer Overflow | 01ROS0018 | BUR0003 | SO | CSO on Sewer Network | SD8450021710 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.07 | 2 | 100%
United Utilities | WATERFOLD LANE CSO | Waterfold Lane CSO | 01ROC0032 | ROC0032 | SO | CSO on Sewer Network | SD8170010050 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Commissioned in 2019 - full year data expected | 725.13 | 86 | 82.19% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WATERHOUSE CLOSE (WARDLE) CSO | Waterhouse Close (Wardle) CSO | 016950075 | ROC0138 | SO | CSO on Sewer Network | SD9138016430 | GB112069064720 | Roch (Source to Spodden) | ASH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 14.93 | 7 | 84.13% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | WATERLOO ROAD CSO (202ZW) | Waterloo Road Sewer | 016820393 | HAL0031 | SO | CSO on Sewer Network | SJ5104083300 | 169 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2020 - full year data expected | 0.3 | 2 | 83.39% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | WATERLOO ST CRESCENT RD CSO | Waterloo Street/Crescent Road CSO | 01MAN0074 | MAN0074 | SO | CSO on Sewer Network | SD8537001580 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | n/a | n/a | Commissioned in 2018 - full year data expected | 39.6 | 36 | 100%
United Utilities | WATERS GREEN (DAMS VALLEY) CSO | Waters Green (Dams Valley) CSO | 01MAC0065 | MAC0065 | SO | CSO on Sewer Network | SJ9195073552 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Commissioned in 2018 - full year data expected | 2.57 | 14 | 100%
United Utilities | WATERS MEETING ROAD CSO 073KZ | Waters meeting Road CSO | 016982261 | BOL0197 | SO | CSO on Sewer Network | SD7196011020 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Commissioned in 2020 - full year data expected | 101.13 | 43 | 90.38% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WATERSIDE COMBINED SEWER OVERFLOW | Waterside CSO | 016982850 | MAC0164 | SO | CSO on Sewer Network | SJ9810086400 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | n/a | n/a | Commissioned in 2018 - full year data expected | 0.67 | 8 | 100%
United Utilities | WATERSIDE CSO 052Z1 | Waterside CSO | 017180721 | BBN0152 | SO | CSO on Sewer Network | SD7156023000 | GB112071065260 | Davyfield Brook | WATERSIDE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | WATERSIDE DRIVE CSO 472H4 | Waterside Drive CSO | 01VRY0057 | VRY0057 | SO | CSO on Sewer Network | SJ5253079050 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Commissioned in 2018 - full year data expected | 45.03 | 25 | 100%
United Utilities | WATERSIDE MILL CSO | Waterside Mill Combined Sewer Overflow | 016950084 | BRY0081 | SO | CSO on Sewer Network | SD7941009510 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Commissioned in 2019 - full year data expected | 4.57 | 4 | 79.75% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | WATERSIDE MILL CSO 212ZY | Waterside Mill CSO | 01PEA0039 | PEA0039 | SO | CSO on Sewer Network | SK0193096510 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | n/a | n/a | Commissioned in 2018 - full year data expected | 0.3 | 6 | 100%
United Utilities | WATERY LANE CSO PRE0108 | Watery Lane CSO | 017180525 | STH0061 | SO | CSO on Sewer Network | SD5198129844 | 176 | #N/A | CHAIN CAUL STORM CULVERT | N/A | N/A | Commissioned in 2019 - full year data expected | 1140.04 | 72 | 98.39% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WATERY LANE CSO PRE0108 | Watery Lane CSO | 017180525 | PRE0108 | SO | CSO on Sewer Network | SD5198129844 | 176 | #N/A | CHAIN CAUL STORM CULVERT | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | WATERY LANE CSO SHAFT C1 PRE0093 | Watery Lane CSO (Shaft C1) | 017180497 | PRE0093 | SO | CSO on Sewer Network | SD5240429937 | 176 | #N/A | MOORBROOK CULVERT -> R. RIBBLE | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | WATERY LANE DOUGLAS ST CSO PRE0110 | Watery Lane/Douglas Street CSO | 017180544 | PRE0110 | SO | CSO on Sewer Network | SD5220029870 | 176 | #N/A | CHAIN CAUL WARD STORM | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WATFORD BRIDGE CSO 212W1 | Watford Bridge CSO | 016982636 | PEA0074 | SO | CSO on Sewer Network | SK0055086410 | GB112069060970 | Sett | RIVER SETT | n/a | n/a | Commissioned in 2018 - full year data expected | 195.57 | 52 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WATLING STREET ROAD CSO 33024 | Watling Street Road CSO | 017180630 | PRE0118 | SO | CSO on Sewer Network | SD5488031380 | GB112071065470 | Savick Brook | EAVES BROOK TRIB SAVICK BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 73.61 | 9 | 100%
United Utilities | WAVERLEY RD CSO 352W4 | Waverley Road CSO | 01ROC0014 | ROC0014 | SO | CSO on Sewer Network | SD8764007330 | GB112069061161 | Irk (Sourtce to Wince Brook) | TRUB BROOK RIVER IRK | North Wirral East | N/A | Commissioned in 2017 - full year data expected | 385.73 | 250 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WAVERTON PUMPING STATION | Waverton PS | 017580266 | ALL0115 | SO | Storm Discharge at Pumping Station | NY2182047150 | GB102075073440 | Waver | RIVER WAVER | n/a | n/a | Commissioned in 2018 - full year data expected | 668.14 | 56 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WEAVERHAM STW | WEAVERHAM WwTW | 016810113 | 16810113 | SO | Inlet CSO at WwTW | SJ6115075180 | GB112068060500 | Weaver (Dane to Frodsham) | TRIB OF RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 69.26 | 42 | 99.91% |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks)
United Utilities | WEAVERHAM STW | WEAVERHAM WwTW | 016810113 | 16810113 | ST | Storm Tank at WwTW | SJ6115075180 | GB112068060500 | Weaver (Dane to Frodsham) | TRIB OF RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 95.72 | 21 | 99.87%
United Utilities | WEETON WASTEWATER TREATMENT WORKS | WEETON WwTW | 017260056 | 17260056 | ST | Storm Tank at WwTW | SD3828034840 | GB112072066120 | Hillylaid Pool - Tidal Wyre | TRIB MAIN DYKE | Lune (Wyre) | Fleetwood | Commissioned in 2017 - full year data expected | 480.37 | 117 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WEETON WASTEWATER TREATMENT WORKS | WEETON WwTW | 017260056 | 17260056 | SO | Inlet CSO at WwTW | SD3828034840 | GB112072066120 | Hillylaid Pool - Tidal Wyre | TRIB MAIN DYKE | Lune (Wyre) | Fleetwood | Commissioned in 2017 - full year data expected | 167.81 | 89 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WEIR STREET COMBINED SEWER OVERFLOW | WEIR STREET CSO | 01VRY0102 | VRY0102 | SO | CSO on Sewer Network | SJ6567073230 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WELL ROW CSO 442XK | WELL ROW CSO | 01TAM0141 | TAM0141 | SO | CSO on Sewer Network | SJ9928093690 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Commissioned in 2017 - full year data expected | 0 | 0 | 100%
United Utilities | WELLINGTON HOTEL CSO | WELLINGTON HOTEL CSO | 01ROS0017 | ROS0017 | SO | CSO on Sewer Network | SD8700023100 | GB112069064660 | Irwell (Source to Whitewell Brook) | CULVERTED TRIB OF RIVER IRWELL | N/A | N/A | Commissioned in 2018 - full year data expected | 0.83 | 1 | 100%
United Utilities | WELLINGTON RD NORTH/ | Wellington Road North / Crossley Road CSO | 016982765 | STK0117 | SO | CSO on Sewer Network | SJ8785093180 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | n/a | n/a | Commissioned in 2018 - full year data expected | 138 | 32 | 67.9% | Sensor failure / issue | N/A - Ongoing investigation
United Utilities | WELLINGTON ROAD CSO | WELLINGTON ROAD CSO | 01BBN0024 | BBN0024 | SO | CSO on Sewer Network | SD6729027040 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Commissioned in 2018 - full year data expected | 0.13 | 2 | 96.53%
United Utilities | WELLINGTON ROAD SOUTH CSO | Wellington Road South CSO | 016982671 | STK0106 | SO | CSO on Sewer Network | SJ8930190321 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Commissioned in 2016 - full year data expected | 181.12 | 68 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution
United Utilities | WELWYN DRIVE CSO 37044 | Welwyn Drive CSO | 016982967 | SAL0074 | SO | CSO on Sewer Network | SD7823000150 | GB112069061430 | Folly Brook and Salteye Brook. | FOLLY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 45.87 | 61 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WENSLEY DRIVE PS | Rolleston Road CSO | 016982802 | BBN0041 | SO | CSO on Sewer Network | SJ9205085230 | GB112069060920 | Micker (Norbury) Brook | NORBURY (MICKER) BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 13.34 | 19 | 99.99%
United Utilities | WEST BRADFORD PS | West Bradford WwNPS | 01RIB0031 | RIB0031 | SO | Storm Discharge at Pumping Station | SD7455044190 | GB112071065612 | Ribble DS Stock Beck | WEST BRADFORD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 362.02 | 57 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WEST END/ WHARF ROAD CSO 425F3 | West End Wharf Road CSO | 016982990 | STH0113 | SO | CSO on Sewer Network | SJ5665094800 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 104.43 | 36 | 100%
United Utilities | WEST HEATH PUMPING STATION | West Heath pumping station (13542) (CON0058) | 016981657 | CON0058 | SO | Storm Discharge at Pumping Station | SJ8342063090 | GB112068055370 | Loach Brook | LOACH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 448.86 | 51 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WEST OF DEWHURST FARM CSO 341RS | West of Dewhurst Farm CSO | 01RIB0016 | RIB0016 | SO | CSO on Sewer Network | SD6850034010 | GB112071065710 | Showley Brook | TRIB OF DINCKLEY BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 171.4 | 88 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WEST ROAD CSO 38055 | Weld Road CSO | 01SEF0064 | SEF0064 | SO | CSO on Sewer Network | SD3171016030 | GB641211630001 | Mersey Mouth | IRISH SEA | Ribble | Ainsdale and Southport | Commissioned in 2017 - full year data expected | 0.62 | 2 | 99.99%
United Utilities | WEST STRAND CSO CHAMBER C10 PRE0071 | West Strand CSO | 017190872 | PRE0071 | SO | CSO on Sewer Network | SD5259329501 | 176 | #N/A | CHAIN CAUL CULVERT INTO RIBBLE | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | WEST STRAND PUMPING STATION | West Strand pumping station (WSTST) (COP0094) | 017470158 | COP0094 | SO | Storm Discharge at Pumping Station | NX9630018070 | 356 | #N/A | IRISH SEA | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.92%
United Utilities | WEST STREET CSO | West Street CSO | 016881772 | STA0017 | SO | CSO on Sewer Network | SJ8794057120 | GB112068055360 | Biddulph Brook | TRIB OF BIDDULPH BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 17.17 | 15 | 100%
United Utilities | WESTERN ROAD CSO | WESTERN ROAD CSO | 01TRA0002 | TRA0002 | SO | CSO on Sewer Network | SJ7419094330 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | CARRS DITECH (CULVERT) | N/A | N/A | Commissioned in 2018 - full year data expected | 7.1 | 39 | 100%
United Utilities | WESTHEAD WWTW | WESTHEAD WwTW | 017030014 | 17030014 | ST | Storm Tank at WwTW | SD4414008280 | GB112070064810 | Eller Brook | CASTLE BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 293.92 | 39 | 99.78%
United Utilities | WESTHOUGHTON STW | WESTHOUGHTON WwTW | 016950136 | 16950136 | ST | Storm Tank at WwTW | SD6500003660 | GB112069060820 | Westleigh Brook | TRIB OF HALL LEE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1684.34 | 140 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WESTHOUGHTON STW | WESTHOUGHTON WwTW | 016950136 | 16950136 | SO | Inlet CSO at WwTW | SD6500003660 | GB112069060820 | Westleigh Brook | TRIB OF HALL LEE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 277.28 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WESTHULME HOSPITAL CSO | Westhulme Hospital CSO | 01OLD0034 | OLD0034 | SO | CSO on Sewer Network | SD9063006030 | GB112069061161 | Irk (Sourtce to Wince Brook) | PLUMPTON CLOUGH | N/A | N/A | Commissioned in 2019 - full year data expected | 5.93 | 7 | 100%
United Utilities | WESTLEIGH ETHERSTONE MD CSO 508AP | Westleigh/Etherstone Main Drainage CSO | 016993705 | WIG0069 | SO | CSO on Sewer Network | SJ6475099780 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 45.8 | 16 | 94.34%
United Utilities | WESTLEIGH PARK CSO 502ZF | Westleigh Park CSO | 016993633 | WIG0071 | SO | CSO on Sewer Network | SD6498001600 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 643.27 | 115 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WESTMINSTER ROAD CSO | Westminster Road CSO | 016892096 | MAC0062 | SO | CSO on Sewer Network | SJ9118074470 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Commissioned in 2018 - full year data expected | 596.1 | 108 | 96.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WESTMOORLAND STREET/SCHOLES CSO | WESTMOORLAND STREET / SCHOLES CSO | 01WIG0017 | WIG0017 | SO | CSO on Sewer Network | SD5952006050 | GB112070064780 | Douglas - Mid | CLARINGTON BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WESTNEWTON PS WSTNE ALL0114 | Westnewton pumping station (Site ID WSTNE) (ALL0114) | 017580265 | ALL0114 | SO | Storm Discharge at Pumping Station | NY1318043820 | GB112075073660 | Crookhurst Beck | WEST NEWTON BECK | SILLOTH | Allonby | Commissioned in 2016 - full year data expected | 647.45 | 76 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WESTNEWTON WWTW | West Newton Wastewater Treatment Works (Site ID WESTN) (017570085) | 017570085 | 17570085 | ST | Storm Tank at WwTW | NY1302043630 | GB112075073660 | Crookhurst Beck | WESTNEWTON BECK | SILLOTH | Allonby | Commissioned in 2016 - full year data expected | 678.22 | 52 | 99.57% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WESTON ST VIKING ST CSO BOL0115 | Weston Street/Viking Street CSO | 016983270 | BOL0115 | SO | CSO on Sewer Network | SD7242007900 | GB112069064540 | Middle Brook | JENNY BECK TRIB RVR CROAL | n/a | n/a | Commissioned in 2018 - full year data expected | 185.92 | 71 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WESTY FLUMES 1 SOUTH CSO 489CB | Westy Flumes (1) South CSO | 016982974 | WAR0125 | SO | CSO on Sewer Network | SJ6282088380 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | Commissioned in 2018 - full year data expected | 12.27 | 18 | 99.99%
United Utilities | WETHERAL AND GREAT CORBY WWTW WETHE | WETHERAL & GREAT CORBY WwTW | 017670075 | 17670075 | ST | Storm Tank at WwTW | NY4673055570 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | n/a | n/a | Commissioned in 2017 - full year data expected | 80.29 | 36 | 100%
United Utilities | WHALEY BRIDGE STW | WHALEY BRIDGE WwTW | 016940184 | 16940184 | SO | Inlet CSO at WwTW | SK0125083220 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Commissioned in 2020 - full year data expected | N/A | N/A | 0% | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | Investigation now complete, remedial work due
United Utilities | WHALLEY NEW ROAD CSO | WHALLEY NEW ROAD CSO | 01BBN0014 | BBN0014 | SO | CSO on Sewer Network | SD6895029070 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 0.53 | 3 | 95.54%
United Utilities | WHALLEY OLD RD/PROVIDENCE ST CSO | WHALLEY OLD ROAD / PROVIDENCE STREET CSO | 01BBN0061 | BBN0061 | SO | CSO on Sewer Network | SD6940029330 | GB112071065310 | Blakewater | LITTLE HARWOOD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 7.13 | 7 | 63.59% | Comms failure / issue | N/A - Ongoing investigation |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WHALLEY RANGE / WESLEY STREET CSO | Whalley Range/Westley Street CSO | NPSWQD010693 | BBN0067 | SO | CSO on Sewer Network | SD6893029050 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 100%
United Utilities | WHALLEY RANGE/GRACE STREET CSO | Whalley Range CSO | 01BBN0049 | BBN0049 | SO | CSO on Sewer Network | SD6873028890 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | WHALLEY RANGE/MILLHAM STREET CSO | WHALLEY RANGE / MILLHAM STREET CSO | 01BBN0048 | BBN0048 | SO | CSO on Sewer Network | SD6862028780 | GB112071065310 | Blakewater | RIVER BLAKEWATER VIA SWS | N/A | N/A | Commissioned in 2019 - full year data expected | 0.47 | 3 | 100%
United Utilities | WHALLEY WASTEWATER TREAMENT WORKS | WHALLEY WwTW | 017180634 | 017160014A | ST | Storm Tank at WwTW | SD7200036400 | GB112071065490 | Calder - Pendle Water to conf Ribble | THE RIVER CALDER | N/A | N/A | Commissioned in 2019 - full year data expected | 2462.13 | 131 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WHARF ROAD CSO | Wharf Road | 01STH0109 | STH0109 | SO | CSO on Sewer Network | SJ5656094750 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 6.43 | 6 | 100%
United Utilities | WHARF ROAD CSO 42077 | Wharf Road CSO | 01STH0070 | STH0070 | SO | CSO on Sewer Network | SJ5658094770 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 297.64 | 81 | 99.97% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WHARF STREET CSO | Wharf Street CSO | 01WAR0061 | WAR0061 | SO | CSO on Sewer Network | SJ6084087870 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023 |  |  | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WHARF STREET CSO 44184 | Wharf Street CSO | 016940472 | TAM0040 | SO | CSO on Sewer Network | SJ6084087870 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | n/a | n/a | Commissioned in 2018 - full year data expected | 275.12 | 67 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WHISTON PARK (ECCLESTON PK) CSO | Whiston Eccleston Park CSO | 016983003 | KNW0017 | SO | CSO on Sewer Network | SJ4589089890 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | LONGWOOD MILL BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 166.44 | 44 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WHITBY ROAD COMBINED SEWER OVERFLOW | Whitby Road CSO | 016881598 | ELL0032 | SO | CSO on Sewer Network | SJ4097077103 | 171 | #N/A | MANCHESTER SHIP CANAL | N/A | N/A | Commissioned in 2019 - full year data expected | 0.03 | 1 | 99.73%
United Utilities | WHITCHURCH ROAD SPS | Newhall PS | 016810293 | CRE0025 | SO | Storm Discharge at Pumping Station | SJ6097045530 | GB112068055210 | Sales Brook | SALES BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 50.98 | 9 | 99.89%
United Utilities | WHITE HART INN CSO | White Hart Inn Combined Sewer Overflow | 01PEA0067 | PEA0067 | SO | CSO on Sewer Network | SK0121081350 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Commissioned in 2019 - full year data expected | 180.47 | 32 | 100%
United Utilities | WHITE HORSE YARD CSO 022X9 | White Horse Yard CSO | 01ALL0028 | ALL0028 | SO | CSO on Sewer Network | NY1414041070 | GB112075073640 | Ellen (lower) | TO RAILWAY TRACK DRAIN | n/a | n/a | Commissioned in 2018 - full year data expected | 24.7 | 27 | 100%
United Utilities | WHITE LION BROW CSO | WHITE LION BROW CSO | 01BOL0119 | BOL0119 | SO | CSO on Sewer Network | SD7123009280 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Commissioned in 2019 - full year data expected | 41.77 | 23 | 99.48%
United Utilities | WHITEBEAM WALK CSO 513PX | Whitebeam Walk CSO | 016892263 | WIR0088 | SO | CSO on Sewer Network | SJ2484086900 | GB112068060530 | The Birket including Arrowe Brook and Fender | GREASBY BROOK TRIB ARROW BROOK | n/a | n/a | Commissioned in 2017 - full year data expected | 40.17 | 18 | 95.16%
United Utilities | WHITEGATE WWTW | WHITEGATE WwTW | 016810114 | 16810114 | ST | Storm Tank at WwTW | SJ6315068970 | GB112068060540 | Bogart Brook | PETTYPOOL BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 99.96%
United Utilities | WHITEGATES PUMPING STATION | Whitegates pumping station (41004) (STA0099) | 016881660 | STA0099 | SO | Storm Discharge at Pumping Station | SJ8874060170 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 12.57 | 7 | 99.89%
United Utilities | WHITEHAVEN WWTW | WHITEHAVEN WwTW | 017480351 | 17480351 | SO | Inlet CSO at WwTW | NX9805021130 | GB112074070040 | Lowca Beck | THE IRISH SEA | N/A | N/A | Commissioned in 2019 - full year data expected | 218.16 | 40 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WHITEMORE PUMPING STATION | Whitemore PS | 016881659 | STA0100 | SO | Storm Discharge at Pumping Station | SJ8855061170 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK, TRIB RVR DANE | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 100%
United Utilities | WHITLEY DRIVE CSO | Whiteley Drive CSO | 016993576 | ROC0116 | SO | CSO on Sewer Network | SD8807005120 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 86.81 | 46 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WHITTAMS FARM CSO 342XW | Whittams Farm CSO | 01RIB0020 | RIB0020 | SO | CSO on Sewer Network | SD7219035710 | GB112071065490 | Calder - Pendle Water to conf Ribble | UNNAMED TRIBUTARY RIVER CALDER | N/A | N/A | Commissioned in 2017 - full year data expected | 563.03 | 97 | 85.47% | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WHITTLE BROOK PS | Whittle Brook PS | 01WAR0048 | WAR0048 | SO | Storm Discharge at Pumping Station | SJ5773087300 | 170 | #N/A | MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 84.46 | 34 | 100%
United Utilities | WHITWORTH CSO | 100Metres East of No. 72 Eastgate CSO | 016950442 | ROS0062 | SO | CSO on Sewer Network | SD8814017070 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 448.34 | 77 | 99.91% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WHITWORTH SSO | Cowm Park Way South | 016950443 | ROS0063 | SO | CSO on Sewer Network | SD8830017880 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WHOOLLEY LANE CSO 44024 | Woolley Lane Combined Sewer Overflow (44024) (TAM0142) | 016993525 | TAM0142 | SO | CSO on Sewer Network | SK0070095180 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | n/a | n/a | Commissioned in 2018 - full year data expected | 373.56 | 86 | 97.88% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WIDNES WWTW | WIDNES WwTW | 016983012 | 16983012 | ST | Storm Tank at WwTW | SJ4851082920 | 167 | #N/A | RIVER MERSEY ESTUARY | N/A | N/A | Commissioned in 2019 - full year data expected | 796.6 | 110 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WIGAN CEMETERY COMBINED SEWER OV | Wigan Cemetry CSO | 017081356 | WIG0208 | SO | CSO on Sewer Network | SD5873004030 | GB112070061610 | Poolstock Brook | INCE BROOK | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | WIGAN ROAD CSO 50087 | Wigan Road Shevington CSO | 017091497 | WIG0002 | SO | CSO on Sewer Network | SD5505008310 | GB112070064820 | Douglas - Lower | MILL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 248.89 | 78 | 99.9% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WIGAN ROAD CSO 50087 | Lancaster Lane CSO | 017091497 | CHR0005 | SO | CSO on Sewer Network | SD5505008310 | GB112070064820 | Douglas - Lower | MILL BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 118.61 | 74 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WIGAN ROAD CSO 50087 | Wigan Road/Darby Lane CSO(502YD) (WIG0191) | 017091497 | WIG0191 | SO | CSO on Sewer Network | SD5505008310 | GB112070064820 | Douglas - Lower | MILL BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0.1 | 1 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WIGAN ROAD/SIDDELEY STREET CSO | Wigan Road/Siddeley Street CSO | 016993668 | WIG0064 | SO | CSO on Sewer Network | SD6485000290 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 102.51 | 50 | 99.96% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WIGAN WASTEWATER TREATMENT WORKS | WIGAN (HOSCAR) WwTW | 017081316 | 17081316 | ST | Storm Tank at WwTW | SD4817012020 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2017 - full year data expected | 726.95 | 55 | 99.97% |  |  | Data collection - Tidal / river inundation | Resolved - February
United Utilities | WIGTON WASTEWATER TREATMENT WORKS | WIGTON WwTW | 017570019 | 17570019 | ST | Storm Tank at WwTW | NY2737051370 | GB102075073460 | Pow Beck (Wampool) | RIVER WAMPOOL | N/A | N/A | Commissioned in 2019 - full year data expected | 671.35 | 64 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WILLASTON RELIEF SEWER | Willaston Relief Sewer | 016810794 | ELL0006 | SO | CSO on Sewer Network | SJ3412078180 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | TRIB DIBBINSDALE BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WILLOW LANE SEWAGE PUMPING STATION | Willow Lane Sewage P/S (25032) | 017280342 | LAN0106 | SO | Storm Discharge at Pumping Station | SD4665962201 | 178 | #N/A | RIVER LUNE ESTUARY | Lune (Broadfleet and Plover Scar) and Morecambe Bay East | Morecambe South | Commissioned in 2017 - full year data expected | 180.86 | 36 | 99.56%
United Utilities | WILMSLOW PARK SOUTH CSO | Wilmslow Park South Combined Sewer Overflow (Site ID 272YI) (MAC0047) | 01MAC0047 | MAC0047 | SO | CSO on Sewer Network | SJ8529081251 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Commissioned in 2019 - full year data expected | 0 | 0 | 100%
United Utilities | WILMSLOW RD/BROOK RD CSO | Wilmslow Road/Brook road CSO | 016982985 | MAN0378 | SO | CSO on Sewer Network | SJ8534093480 | GB112069061410 | Fallowfield Brook | LEIGH BROOK | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WILMSLOW STW | WILMSLOW WwTW | 016910014 | 16910014 | ST | Storm Tank at WwTW | SJ8413082320 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | n/a | n/a | Commissioned in 2018 - full year data expected | 1573.25 | 170 | 99.83% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WILMSLOW STW | WILMSLOW WwTW | 016910014 | 16910014 | SO | Inlet CSO at WwTW | SJ8413082320 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | n/a | n/a | Commissioned in 2018 - full year data expected | 359.12 | 73 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WILPSHIRE WWTW (WILPS) | WILPSHIRE WwTW | 017160049 | 17160049 | ST | Storm Tank at WwTW | SD6755032440 | GB112071065710 | Showley Brook | SHOWLEY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 1161.2 | 105 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WINDBOURNE CSO | Windbourne CSO | 01LIV0044 | LIV0044 | SO | CSO on Sewer Network | SJ3678086240 | 167 | #N/A | RIVER MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 8.23 | 5 | 100%
United Utilities | WINDMILL LANE CSO 44012 | Windmill Lane CSO | 016983013 | TAM0172 | SO | CSO on Sewer Network | SJ9115094820 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA CLVR WCOURSE | n/a | n/a | Commissioned in 2018 - full year data expected | 30.66 | 5 | 99.96%
United Utilities | WINDSOR GROVE | Windsor Grove CSO | 01HAL0126 | HAL0126 | SO | CSO on Sewer Network | SJ5188081850 | 169 | #N/A | #N/A | N/A | N/A | Commissioned pre-2016 - full year data expected | 0 | 0 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation
United Utilities | WINDSOR ROAD/WINTERDYNE STREET CSO | WINDSOR ROAD / WINTERDYNE STREET CSO | 01MAN0082 | MAN0082 | SO | CSO on Sewer Network | SD8618001260 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.13 | 1 | 100%
United Utilities | WINNINGTON STREET CSO 472YM | Winnington Street CSO | 01VRY0077 | VRY0077 | SO | CSO on Sewer Network | SJ6567073870 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | n/a | n/a | Commissioned in 2018 - full year data expected | 35.17 | 34 | 99.59%
United Utilities | WINSFORD HILL STREET | Hill Street PS | 016892221 | VRY0090 | SO | Storm Discharge at Pumping Station | SJ6555066270 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Commissioned in 2020 - full year data expected | 83.63 | 18 | 100%
United Utilities | WINSFORD WASTEWATER TREATMENT WORKS | WINSFORD WwTW | 016810116 | 16810116 | ST | Storm Tank at WwTW | SJ6544067440 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Commissioned in 2016 - full year data expected | 232.35 | 46 | 99.74% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WINSFORD WASTEWATER TREATMENT WORKS | WINSFORD WwTW | 016810116 | 16810116 | SO | Inlet CSO at WwTW | SJ6544067440 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Commissioned in 2016 - full year data expected | 61.69 | 24 | 99.74%
United Utilities | WINSKILL PUMPING STATION | Winskill PS | EPRFP3523XL | EDE0122 | SO | Storm Discharge at Pumping Station | NY5756034680 | GB102076073800 | Briggle Beck | BRIGGLE BECK | N/A | N/A | Commissioned in 2019 - full year data expected | 12.8 | 4 | 99.85%
United Utilities | WINSTANLEY ROAD PUMPING STATION | Winstanley Road PS | 017020090 | WIG0155 | SO | Storm Discharge at Pumping Station | SD5327003840 | GB112070061600 | Smithy Brook | SMITHY BROOK | n/a | n/a | Commissioned in 2018 - full year data expected | 0.17 | 3 | 99.99%
United Utilities | WINSTON DRIVE HENSINGHAM CSO 02632 | Winston Drive CSO | 017480428 | COP0005 | SO | CSO on Sewer Network | NX9864016940 | 356 | #N/A | SNEBRA BECK | n/a | n/a | Commissioned in 2018 - full year data expected | 39.57 | 24 | 99.36%
United Utilities | WINTON OUTFALL | Winton Outfall CSO | 016993656 | SAL0018 | SO | CSO on Sewer Network | SJ7537097600 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 0 | 0 | 36.81% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | WINTON PUMPING STATION | Winton PS | 017670197 | EDE0064 | SO | Storm Discharge at Pumping Station | NY7760010530 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Commissioned in 2019 - full year data expected | 2190.69 | 162 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WISTASTON ROAD CSO | Wistaston Road CSO | 01CRE0038 | CRE0038 | SO | CSO on Sewer Network | SJ6975055440 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 0 | 0 | 29.46% | Comms failure / issue | N/A - Ongoing investigation
United Utilities | WITHINGTON PUMPING STATION 28009 | Withington PS | 01MAN0250 | MAN0250 | SO | Storm Discharge at Pumping Station | SJ8091092840 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | n/a | n/a | Commissioned in 2017 - full year data expected | 558.27 | 110 | 99.94% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WITHNELL FOLD NETWORK PUMPING STATI | Withnell Fold PS | 01CHR0065 | CHR0065 | SO | Storm Discharge at Pumping Station | SD6130023570 | GB112070064911 | Lostock US Farington Weir | KYLN CLOUGH, TRIB OF R LOSTOCK | N/A | N/A | Commissioned in 2019 - full year data expected | 1763.5 | 129 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WITTON TANKS CSO | Witton Tanks CSO | 017180642 | BBN0089 | SO | CSO on Sewer Network | SD6672027570 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Commissioned in 2020 - full year data expected | 124.73 | 56 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WODOW ROAD COMBINED SEWER OVERFLOW | Wodow Road CSO | 01COP0038 | COP0038 | SO | CSO on Sewer Network | NY0075008871 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Commissioned in 2016 - full year data expected | 1.4 | 7 | 100%
United Utilities | WOLSELEY ROAD CSO | Wolseley Road CSO | 017160324 | PRE0028 | SO | CSO on Sewer Network | SD5311028280 | 176 | #N/A | RIVER RIBBLE | Ribble | Southport, St Annes Pier, St. Annes North and Blackpool South | Commissioned in 2018 - full year data expected | 73.74 | 9 | 100%
United Utilities | WOOD LANE/GLENTREE CLOSE CSO | Wood Lane/ Glentree Close CSO | 016892444 | WIR0083 | SO | CSO on Sewer Network | SJ2556188181 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK TRIB R. BIRKETT | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WOOD STREET CSO | Wood Street CSO | 016982644 | ROC0168 | SO | CSO on Sewer Network | SD8658006240 | GB112069061161 | Irk (Sourtce to Wince Brook) | RIVER IRK | N/A | N/A | Commissioned in 2017 - full year data expected | 397.73 | 102 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WOOD STREET CSO | Lancaster Bus Station CSO | 016982644 | LAN0077 | SO | CSO on Sewer Network | SD8658006240 | GB112069061161 | Irk (Sourtce to Wince Brook) | RIVER IRK | Morecambe Bay East and Lune (Broadfleet and Plover Scar) | Morecambe South | Commissioned in 2017 - full year data expected | 47.54 | 16 | 100% |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
United Utilities | WOOD TOP FARM GRINSAGH | Osbaldeston PS | 01RIB0008 | RIB0008 | SO | Storm Discharge at Pumping Station | SD6428031930 | GB112071065500 | Ribble - conf Calder to tidal | UNNAMED TRIB OF BEZZA BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 4.71 | 2 | 100%
United Utilities | WOODBARN FARM CSO 07059 | Wood Barn Farm CSO | 017091505 | BOL0141 | SO | CSO on Sewer Network | SD6209010990 | GB112070064850 | Douglas - Upper | UNNAMED TRIB THE RIVER DOUGLAS | n/a | n/a | Commissioned in 2018 - full year data expected | 167.95 | 72 | 98.32% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WOODBROOK ROAD CSO | Woodbrook Road CSO | 01OLD0113 | OLD0113 | SO | CSO on Sewer Network | SD9671005270 | GB112069061151 | Medlock (Source to Lumb Brook) | WOOD BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.37 | 1 | 100%
United Utilities | WOODHILL ROAD CSO 092JP | Woodhill Road CSO | 01BRY0012 | BRY0012 | SO | CSO on Sewer Network | SD7971011340 | GB112069064610 | Kirklees Brook | WOODHILL BROOK | N/A | N/A | Commissioned in 2018 - full year data expected | 5.4 | 4 | 100%
United Utilities | WOODHOUSE ROAD CSO 459BC | Woodhouse Road CSO | 016993438 | TRA0005 | SO | CSO on Sewer Network | SJ7534095800 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BRK BENT LANES BRK | n/a | n/a | Commissioned in 2018 - full year data expected | 139.37 | 39 | 100%
United Utilities | WOODLANDS CLOSE CSO (21117) | Woodlands Close CSO | 01PEA0042 | PEA0042 | SO | CSO on Sewer Network | SK0167096890 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Commissioned in 2020 - full year data expected | 584.94 | 103 | 99.95% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WOODLANDS GROVE CSO | Woodlands Grove CSO | 01VRY0052 | VRY0052 | SO | CSO on Sewer Network | SJ6282075520 | GB112068060510 | Cogshall Brook | TRIB OF TRENT & MERSEY CANAL | N/A | N/A | Commissioned in 2018 - full year data expected | 23.53 | 46 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WOODSIDE CSO | Woodside CSO | 016931348 | WIR0116 | SO | CSO on Sewer Network | SJ3298089260 | GB531206908100 | MERSEY | MERSEY ESTUARY | NORTH WIRRAL (EAST) | New Brighton | Commissioned in 2016 - full year data expected | 582.57 | 69 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WOODVALE FLATS CSO | Woodvale Flats combined sewer overflow (059AF) (BBN0151) | 017180476 | BBN0151 | SO | CSO on Sewer Network | SD6888022570 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | n/a | n/a | Commissioned in 2018 - full year data expected | 0.97 | 13 | 100%
United Utilities | WOOLLEY BRIDGE ROAD CSO 43133 | Woolley Bridge Road CSO | 016993681 | PEA0069 | SO | CSO on Sewer Network | SK0124096020 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | n/a | n/a | Commissioned in 2018 - full year data expected | 180.93 | 60 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WOOLLEY BRIDGE SPS | Spring Tavern CSO | 016982492 | PEA0036 | SO | CSO on Sewer Network | SK0092095820 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | n/a | n/a | Commissioned in 2018 - full year data expected | 390.73 | 72 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue"
United Utilities | WOOLTON STW | Woolton WwTW | 016930122 | 16930122 | ST | Storm Tank at WwTW | SJ4495087460 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | HALEWOOD BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 262.87 | 35 | 100%
United Utilities | WOOLTON STW | Woolton WwTW | 016930122 | 16930122 | SO | Inlet CSO at WwTW | SJ4495087460 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | HALEWOOD BROOK | N/A | N/A | Commissioned in 2020 - full year data expected | 20.4 | 14 | 100%
United Utilities | WORKINGTON WWTW | WORKINGTON WwTW | 017580285 | 17580285 | SO | Inlet CSO at WwTW | NY0048031840 | 357 | #N/A | IRISH SEA | N/A | N/A | Commissioned in 2020 - full year data expected | 943.66 | 129 | N/A | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WORSLEY STW | WORSLEY WwTW | 016940139 | 16940139 | SO | Inlet CSO at WwTW | SD7215002750 | GB112069061100 | Astley Brook (Mersey) | LITTLE HULTON STREAM | N/A | N/A | Commissioned in 2019 - full year data expected | 495.95 | 89 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WORSLEY STW | WORSLEY WwTW | 016940139 | 16940139 | ST | Storm Tank at WwTW | SD7215002750 | GB112069061100 | Astley Brook (Mersey) | LITTLE HULTON STREAM | N/A | N/A | Commissioned in 2019 - full year data expected | 748.69 | 82 | 99.98% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | WORSLEY STW | WORSLEY WwTW | 016940139 | 16940139 | SO | Inlet CSO at WwTW | SD7215002750 | GB112069061100 | Astley Brook (Mersey) | LITTLE HULTON STREAM | N/A | N/A | Commissioned in 2019 - full year data expected | 51.24 | 18 | 99.42%
United Utilities | WRAY WASTEWATER TREATMENT WORKS | Wray Wastewater Treatment Works (WRAYZ) (017270020) | 017270020 | 17270020 | SO | Inlet CSO at WwTW | SD6011068120 | GB112072066050 | Hindburn | RIVER HINDBURN | n/a | n/a | Commissioned in 2018 - full year data expected | 312.64 | 209 | 99.88% |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Resolved - December
United Utilities | WREAY WWTW WREAY | WREAY WwTW | 017680463 | 17680463 | SO | Inlet CSO at WwTW | NY4366248788 | GB102076074030 | Petteril d/s Blackrack Beck | THE RIVER PETTERIL | n/a | n/a | Commissioned in 2018 - full year data expected | 0 | 0 | 99.99%
United Utilities | WRENBURY HALL ROAD SPS | Wrenbury Hall Road PS | 016810369 | CRE0028 | SO | Storm Discharge at Pumping Station | SJ6010048400 | GB112068055470 | Weaver (Marbury Brook to Barnett Brook) | SHROPSHIRE UNION CANAL | N/A | N/A | EDM to be installed by December 2023 | N/A | N/A | N/A | EDM not yet installed | N/A - EDM to be installed by December 2023
United Utilities | WRENBURY WASTEWATER TREATMENT WORKS | WRENBURY WwTW | 016810119 | 16810119 | SO | Inlet CSO at WwTW | SJ6077047561 | GB112068055470 | Weaver (Marbury Brook to Barnett Brook) | RIVER WEAVER | n/a | n/a | Commissioned in 2018 - full year data expected | 88.13 | 27 | 99.89%
United Utilities | WYBUNBURY PS | Wynbunbury CSO (EO for 16014 - The Cliffe PS) 16CSO002 | 016881683 | CRE0044 | SO | Storm Discharge at Pumping Station | SJ7012049610 | GB112068055240 | Checkley Brook - Lower | WYBUNBURY BROOK | N/A | N/A | Commissioned in 2019 - full year data expected | 0.13 | 1 | 96.75%
United Utilities | WYNDHAM TERRACE CSO | Wyndham Terrace CSO | 01COP0028 | COP0028 | SO | CSO on Sewer Network | NY0128011300 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Commissioned in 2016 - full year data expected | 1.97 | 9 | 100%
United Utilities | YORK AVE/CRAWFORD AVENUE CSO | York Avenue CSO | 016993565 | WIG0086 | SO | CSO on Sewer Network | SD6873002580 | GB112069060810 | Bedford Brook | HINDSFORD BROOK/SHAKERLEY BROO | N/A | N/A | Commissioned in 2020 - full year data expected | 1549.37 | 115 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | YORK AVE/CRAWFORD AVENUE CSO | York Avenue CSO | 016993565 | WIG0086 | SO | CSO on Sewer Network | SD6873002580 | GB112069060810 | Bedford Brook | HINDSFORD BROOK/SHAKERLEY BROO | N/A | N/A | Commissioned in 2020 - full year data expected | 40.66 | 33 | 100%
United Utilities | YORKSHIRE ST OSWALD ST CSO 35024 | Yorkshire Street / Oswald Street CSO | 016993538 | ROC0067 | SO | CSO on Sewer Network | SD9044014030 | GB112069064720 | Roch (Source to Spodden) | HEY BROOK TRIB OF RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 55.37 | 44 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity
United Utilities | YORKSHIRE STREET CSO 35022 | Yorkshire Street CSO | 01ROC0058 | ROC0058 | SO | CSO on Sewer Network | SD8962013380 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | n/a | n/a | Commissioned in 2018 - full year data expected | 42.02 | 16 | 99.79%
United Utilities | ZULU SREET CSO 07032 | Zulu Street CSO | 016983222 | BOL0109 | SO | CSO on Sewer Network | SD7288009270 | GB112069064530 | Tonge | RIVER TONGE | n/a | n/a | Commissioned in 2018 - full year data expected | 31.32 | 43 | 100% |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity

## Drop Downs - SO (hidden)
Storm discharge asset type | Initial EDM Commission Date | EDM Operation - Reporting percentage - Primary Reason <90% | EDM Operation - Action taken / planned - Status & Timeframe | High Spill Frequency - Operational Review - Primary Reason (Asset Maintenance) | High Spill frequency - Action taken / planned - Status & Timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic Capacity)
SO on sewer network | Installed but not yet commissioned | Access - Unable to retrieve data from non-telemetry data logger (NB: not to be used for delayed access to fix existing fault) | Scheduled | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Scheduled | SOAF N/A - Proposed SFTP (overflow previously improved)
Storm discharge at pumping station | Commissioned in 2020 - full year data expected | Capital / maintenance works affect EDM operation | Resolved - January | Performance - Sewer collapse (partial / full) - infrastructure issue | Resolved - January | Stage 1a: Confirmed "exceptional weather" issue
Inlet SO at WwTW | Commissioned in 2019 - full year data expected | Comms failure / issue | Resolved - Feburary | Performance - GW inundation | Resolved - Feburary | Stage 1b: Confirmed "asset maintenance" issue
Storm tank at WwTW | Commissioned in 2018 - full year data expected | EDM not yet installed | Resolved - March | Performance - Infiltration | Resolved - March | Stage 1c: Confirmed "hydraulic issue"
Other storm discharge asset type | Commissioned in 2017 - full year data expected | EDM installed - not yet commissioned | Resolved - April | Performance - Asset power failure | Resolved - April | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal
| Commissioned in 2016 - full year data expected | Installation set-up/design issue | Resolved - May | Performance - Pump failure / issue | Resolved - May | U_INV driver - Stage 4: Cost beneficial outcome not yet determined
| Commissioned pre-2016 - full year data expected | Power failure / issue | Resolved - June | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - June | U_INV driver - Stage 4: No cost beneficial solution
| Jan 2021 | Sensor failure / issue | Resolved - July | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - July | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP7 or Green Recovery
| Feb 2021 | Telemetry or data archiving failure / issue | Resolved - August | Data collection - EDM non-representative location | Resolved - August | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP7 or Green Recovery
| Mar 2021 | No longer operational as an overflow - permit revoked or to be revoked | Resolved - September | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | Resolved - September | N/A - Operational solution applied
| April 2021 |  | Resolved - October | Data collection - Tidal / river inundation | Resolved - October
| May 2021 |  | Resolved - November | Not asset maintenance - Hydraulic capacity | Resolved - November
| June 2021 |  | Resolved - December |  | Resolved - December
| July 2021 |  | N/A - Ongoing investigation |  | N/A - Ongoing investigation
| August 2021 |  | N/A - EDM to be installed by December 2023 |  | N/A - Hydraulic capacity
September 2021
October 2021
November 2021
December 2021
EDM to be installed by December 2023