## Sheet1
Please provide details of all incidents classified by United Utilities as “major” or “critical” during the period 1 January 2022 to 31 January 2024, including (where held):
The date(s) of each incident
The location (site, catchment, or operational area)
The nature of the incident (e.g. pollution, service failure, asset failure, supply or treatment disruption)
The environmental impact, including any discharges, pollution events, or risks to water quality, ecosystems, or public health
Any regulatory notifications made (for example to the Environment Agency or other regulators)
Any incident classification framework or criteria used by United Utilities to define “major” or “critical” incidents during this period
Below is a list of drinking water quality events categorised by the Drinking Water Inspectorate (DWI) as serious or major. Unlike with Environmental incidents, the categorisation of drinking water quality events is always assigned by the DWI, never the Water Company.
Event date | Event Name | Location | Nature of the incident | Environmental impact | Regulatory notifications | Incident classification
2023-03-24 | Talbot Bridge Do Not Drink | 10 properties in Talbot Bridge | From 15 March 2023 to 22 March 2023, we received six water quality contacts from properties located in Talbot Bridge reporting a 'musty' taste and odour and a discoloured appearance to their water supply. In response to the contacts, the Company arranged for water quality samples to be collected and for network investigations to be instigated. Following a review of sample results and in liaison with UK Health Security Agency – Cumbria and Lancashire Health Protection Team, the Company issued do not drink advice to 10 properties. A submerged air valve was identified which is considered the likely cause. Work was carried out to replace the air valve and install risers to ensure that the air valve remains above the ground water level. | Public Health risk identified from contamination source to the drinking water supply. Do not drink advice issued to proect consumers. | Drinking Water Inspectorate | Serious - classified by the DWI
2023-04-26 | Wallasey Discoloured Water (Green) | A discreet area of Wallasey (Leasowe Road and Heyes Drive) | From 29 March to 23 May 2023 consumers in a housing estate and two commercial properties in the Leasowe Road area of Wallasey experienced intermittent green discoloured water. The cause of the green water was a cross connection between the company network and an open storage tank at a commercial plant nursery, which was disconnected by the company on 23 May 2023. A boil water notice was issued to a commercial complex in the affected area. | Public Health risk identified from third party contamination source to the drinking water supply. Do not drink advice issued to proect consumers. | Drinking Water Inspectorate | Serious - classified by the DWI
2023-03-09 | Oswestry WTW Interruption to Reg 26 Monitoring | Oswestry Water Treatment Works | A blown fuse in one of the site’s motor control centre panels, caused a temporary loss of flow to the Regulation 26 instruments at the contact tank inlet on Stream 1 of the works. The treatment works as a whole was unaffected. This reoccurred on Monday 13 March 2023, when the replacement fuse failed. In both instances, site personnel swiftly identified the loss of flow to the instruments and began to investigate the cause. A power supply and flow to the instruments was reinstated within five and a half hours on the first occasion and four hours on the second. The Company is confident that, through surrogate upstream and downstream monitoring, we can demonstrate compliance with Regulation 26 throughout both periods of loss of monitoring. | None | Drinking Water Inspectorate | Serious - classified by the DWI
2023-07-06 | Rossendale Wastewater Treatment Works Do Not Drink | Rossendale Wastewater Treatment Works | Personnel at Rossendale Waste Water Treatment Works noted discolouration to the domestic supply. Initial investigations indicate that an inadvertent cross connection had been made between an on-site non-potable supply and the ‘domestic’ water system. Company staff and contractors on site were advised not to use the supply for drinking, washing of wounds or for food preparation until further notice, whilst investigations were carried out. Bottled water was supplied for drinking and an temporary tank was delivered to site providing a supply for hand washing. The Company confirmed the presence of backflow protection at the boundary of the site and a sampling survey confirmed that the contamination was confined to the site’s facilities only. Samples from customer properties both upstream and downstream of the works were satisfactory. The domestic distribution system was flushed from all draw off points and chlorinated. The advice was rescinded on completion of this and receipt of two sets of satisfactory sample results. | Public Health risk identified from contamination source to the drinking water supply. Do not drink advice issued to proect consumers. | Drinking Water Inspectorate | Serious - classified by the DWI
2023-08-15 | Lightshaw Customer Contacts | Leigh | In July 2023, Lightshaw WTW was returned to supply feeding parts of Leigh and Haydock. Lightshaw WTW has historically been a significant supply in these areas, but is taken out of supply from time to time for operational reasons. Being a groundwater site, water from Lightshaw WTW is harder compared to the other supplies that can feed these zones. Therefore, we proactively notify customers in these areas of any proposed change to their water supply after any prolonged outage. Throughout August 2023 we received an unprecedented 366 complaint letters from customers in the WN7 4 area of Leigh. | None | Drinking Water Inspectorate | Serious - classified by the DWI
2024-01-23 | Cheshire and Merseyside Customer Contacts | Areas of Cheshire and Merseyside | Upon notification of a pollution event on the River Dee (DEEPOL), we swiftly initiated our established incident procedure with associated mitigating actions at the two works receiving a supply from the River Dee, Huntington WTW and Sutton Hall WTW. Subsequently, we received customer contacts from areas supplied by the works reporting taste and odours to their supply, primarily with chlorine/TCP descriptors . The works provide a supply of water to a large area of Cheshire and Merseyside; between 19 January and 24 January 2024, we received 39 customer contacts, 26 noted a TCP/chlorine descriptor. Of those 26 contacts, 92% were received from zones supplied by Huntington WTW. The total population supplied by the works is 1,904,568. Contacts were received from 0.002% of the population supplied. Investigations identified that, in the week prior to the DEEPOL event, the level in the River Dee had dropped sufficiently to allow flood water from the catchment to flow back into the River. The flood water is likely to have been ‘held back’ on the fields for several weeks, by the elevated river level, before being able to drain away, transferring an accumulation of potential contaminants into the river. The Company does not believe that the event is related to a specific contamination incident. | None | Drinking Water Inspectorate | Serious - classified by the DWI