United Utilities Water

Meter Selection Catalogue

Table of Contents

Foreword.	3

Operating principles of different meter types	4

Available Meters	5

Flow Data	8

Pulse Unit Information	11

Elster Bulk Meter Product selector	16

Foreword.

This document contains a catalogue of water meters which are approved for use by United Utilities Water (UUW) for fiscal use, and these meters may be selected by a new Water Supply Licensee (WSL).

Only water meters contained within this document are available for selection.  UUW will not accept the installation of any alternative water meter as a fiscal meter.

All water meters will be provided by UUW.  The WSL will have a role in selecting the preferred meter to be used.

This document should be read in conjunction with the following documentation:-

- Operating Code OC1 – Pulsed Output

- Operating Code OC2 – Meter Size Change

- Operating Code OC3 – Meter Testing

- Operating Code OC4 – Alterations to meter location or housing

- Operating Code OC5 – Maintenance activity required

- Operating Code OC6 – Failure of data logging equipment

- Wholesale Supply Common Contract

This document facilitates Licensee requests to upsize, downsize or exchange existing water meters as described in Section 7 ; Section 12 of the Wholesale Supply Common Contract.

# Operating principles of different meter types

.

Piston meter (Volumetric).

Piston meters, also known as rotary piston or semi-positive displacement meters, the piston meter operates on the principle of a piston rotating within a chamber of known volume. For each rotation, an amount of water passes through the piston chamber. Through a gear mechanism and, sometimes, a magnetic drive, a needle dial and odometer type display is advanced.

- Accurate at low flow

- Low maintenance

Single jet meter

- A single jet meter consists of a simple impeller with radial vanes, impinged upon by a single jet. A magnetic coupling to the register drives directly off the rotor and a needle dial and odometer type display are advanced.

- Low to Medium range meter

- Low headloss across meter

Woltmann meter

The Woltmann meter comprises a rotor with helical blades inserted axially in the flow, much like a ducted fan; it can be considered a type of turbine flow meter. They are commonly referred to as helix meters, and are popular at larger sizes. A magnetic coupling to the register drives directly off the rotor and a needle dial and odometer type display are advanced.

- High flow range meter

- Horizontal or Vertical Installation

Combination Meters

Combination meters combined a volumetric meter and a Voltmann meter in one meter body. During periods of low flow the water is recorded through the volumetric meter. When the flow increases a changeover valve diverts the water through the Voltmann meter.

- Low to high flow range meter

- Suitable for low consumption customers with firefighting facilities

- Horizontal or Vertical Installation

- Magnetic flow meters

Magnetic flow meters, often called "mag meter’s” or "electromag’s”, use a magnetic field applied to the metering tube, which results in a potential difference proportional to the flow velocity perpendicular to the flux lines. The potential difference is sensed by electrodes aligned perpendicular to the flow and the applied magnetic field. The physical principle at work is Faraday's law of electromagnetic induction.

- Battery or mains powered

- Bi directional

- Do not require strainers

- No mechanical measuring element

- Suitable for non-potable water

# Available Meters

The following meters are available for selection and accepted by UUW.

Size 15mm / 20mm - Sappel Altair (Piston)

- Accurate at low flows

- Supplied with AMR unit attached & paired to meter

- Sizes available – 15mm & 20mm.

- Flow ranges from 5 litres/hr – 5 m3/hr

- Composite meter body

Size 25mm / 40mm  - Elster V100 (Piston)

- Accurate at low flows

- Reliable, low maintenance

- Sizes available – 25mm & 40mm

- Flow range from 35 litres/hr – 20 m3/hr

- Magnetic Pulse output available (5 litres/pulse)

- T-Probe pulse unit

Size 25mm / 40mm - Elster V200 (Piston)

- Accurate at low flows

- Reliable, low maintenance

- Sizes available – 25mm & 40mm

- Flow range from 39.37 litres/hr – 12.5 m3/hr

- Inductive Pulse output (Primary & Secondary available)

- PR6 Pulse Unit

Size 50mm / 100mm  Elster S2000 (Single Jet)

- Low – Mid flow rate meter

- Low headloss across meter

- Sizes available – 50mm/80mm/100mm

- Flow range from – 90 litres/hr – 100 m3/hr

- Inductive Pulse output (Primary & Secondary available)

- PR7 Pulse unit

Size 50mm – 150mm Elster H4000 (Woltmann)

- High flow rate meter

- Sizes available – 50mm/80mm/100mm/150mm.

- Flow range from – 0.35 m3/hr – 600 m3/hr

- Inductive Pulse output (Primary & Secondary available)

- PR7 Pulse unit

Size 50mm – 150mm Elster H5000 (Woltmann)

- Wide measuring range

- Retro-fit mechanism into the H4000 body

- Electronic register includes an integrated communications cable

- Electronic register pre-equipped for AMR

- AMR features such as flow rate display, leak detection, tamper alarms and tariffing

- Sizes available 50mm/80mm/100mm/150mm.

- Flow range from 50 litres/hr – 200 m3/hr

Size 50mm – 150mm Elster C4000 (Combination)

- Accurate for large variations in flow rate

- Sizes available – 50mm/80mm/100mm/150mm*

- Primary and Secondary pulsed outputs available on both dials

- Main meter – PR7 Pulse unit

- By-pass – PR6 Pulse unit

Size 50mm – 200mm Elster Q4000 (Electromagnetic)

- Electromagnetic meter

- Low headloss across meter

- Low – high flow range

- Bi-directional pulsed output (2 outputs if using the remote display)

- Suitable for non-potable water

- Sizes available 50 – 200 mm

- Flow range from 0.10 m3/hr – 788 m3/hr

Size 50mm – 300mm ABB AquaMaster (Electromagnetic)

- Electromagnetic meter

- Low headloss across meter

- Low – high flow range

- User defined pulsed output

- Suitable for non-potable water

- Sizes available 50 – 300 mm

- Flow range from 0.10 m3/hr – 788 m3/hr

Size 50mm – 500mm ABB WaterMaster (Electromagnetic)

- Electromagnetic meter

- Low headloss across meter

- Low – high flow range

- User defined pulsed output

- Suitable for non-potable water

- Sizes available 50 – 500 mm

- Flow range from 0.10 m3/hr – 788 m3/hr

Flow Data

# Flow Data

| Size | Operating Type | UU recommended Flow Range (overload flow) | Meters Available | Compliance Standards | Output Capability | Number of Outputs Available | Pulse Splitter Compatible |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 15mm | Piston (in-line) | 5 l/hr – 3.125 m3/hr | Sappel Altair V3 | EN14154, OIML R49, ISO 4064, MID, WIS | AMR meter, no available free output. Requires pulse splitter installation. | 1 (with AMR unit removed) | Yes with specific pulse unit |
|  | Piston (Concentric) | 5 l/hr – 3.125 m3/hr | Sappel Altair V4 | EN14154, OIML R49, ISO 4064, MID, WIS |  | 1 (with AMR unit removed) | Yes with specific pulse unit |
| 20mm | Piston (in-line) | 25 l/hr – 5 m3/hr | Sappel Altair V3 | EN14154, OIML R49, ISO 4064, MID, WIS | AMR meter, no available free output Requires pulse splitter installation. | 1 (with AMR unit removed) | Yes with specific pulse unit |
|  | Piston (Concentric) | 25 l/hr – 5 m3/hr | Sappel Altair V4 | EN14154, OIML R49, ISO 4064, MID, WIS |  | 1 (with AMR unit removed) | Yes with specific pulse unit |
| 25mm | Piston | 35 l/hr – 3.5 m3/hr (7 m3/hr) | Elster V100 | ISO4064, EEC Directive 75/33/EEC, BS5728 Class C | T probe, 5 litres/pulse | 1 | Yes |
|  |  | 39 l/hr – 6.3 m3/hr (7.8 m3/hr) | Elster V200 | (MID) Directive 2004/22/EC OIML R49 | PR6 unit, recommend K 1:1 | 2 | Yes |
| 40mm | Piston | 100 l/hr – 10 m3/hr (20 m3/hr) | Elster V100 | ISO4064, EEC Directive 75/33/EEC, BS5728 Class C | T probe, 5 litres/pulse | 1 | Yes |
|  |  | 100 l/hr – 10 m3/hr (12.5 m3/hr) | Elster V200 | (MID) Directive 2004/22/EC OIML R49 | PR6 unit, recommend K 1:1 | 2 | Yes |
| 50mm | Single Jet | 90 l/hr – 15 m3/hr (30 m3/hr) | Elster S2000 | ISO4064, BS5728 Class C | PR7 unit, dual output | 2 | Yes |
|  | Woltmann | 0.75 m3/hr – 15 m3/hr (30 m3/hr) | Elster H4000 | ISO4064/BS5728/EEC specification Class B | recommend using K 10:10 | 2 | Yes |
|  |  | 0.05 m3/hr – 63 m3/hr (79 m3/hr) | Elster H5000 | (MID) Directive 2004/22/EC | Integrated communication cable. | 2, or 4 with splitter | Yes |
|  | Combination | 15 l/hr – 25 m3/hr (50 m3/hr) | Elster C4000 | (MID) Directive 2004/22/EC | Main meter - PR7, Low flow meter - PR6 unit | 2 (on each) | Yes |
|  | Electromagnetic | 0.1 m3/hr – 40 m3/hr (50 m3/hr)** | Elster Q4000 | (MID) Directive 2004/22/EC | MX39 dual output Pulser or MX35 dual output remote display | 2 | Yes |
|  |  | 0.25 m3/hr – 40 m3/hr (50 m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 0.2 m3/hr – 63 m3/hr (79 m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |

| 80mm | Single Jet | 180 l/hr – 30 m3/hr (60 m3/hr) | Elster S2000 | ISO4064, BS5728 Class C | PR7 unit 10 litres/pulse, dual output | 2 | Yes |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Woltmann | 1.2 m3/hr – 40 m3/hr (80 m3/hr) | Elster H4000 | ISO4064/BS5728/EEC specification Class B | recommend using K 10:10 | 2 | Yes |
|  |  | 0.05 m3/hr – 63 m3/hr (79 m3/hr) or 0.13 m3/hr - 160 m3/hr (200 m3/hr) | Elster H5000 | (MID) 2004/22/EC | Integrated communication cable. | 2, or 4 with splitter | Yes |
|  | Combination | 15 l/hr – 40 m3/hr (80 m3/hr) | Elster C4000 | (MID) Directive 2004/22/EC | Main meter - PR7, Low flow meter - PR6 unit | 2 (on each) | Yes |
|  | Electromagnetic | 0.25 m3/hr – 100m3/hr (125m3/hr)** | Elster Q4000 | (MID) Directive 2004/22/EC | MX39 dual output Pulser or MX35 dual output remote display | 2 | Yes |
|  |  | 0.63 m3/hr – 100 m3/hr (125 m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 0.51 m3/hr – 160 m3/hr (200 m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |
| 100mm | Single Jet | 300 l/hr – 50 m3/hr (100 m3/hr) | Elster S2000 | ISO4064, BS5728 Class C | PR7 unit 10 litres/pulse, dual output | 2 | Yes |
|  | Woltmann | 1.8 m3/hr – 60 m3/hr (120 m3/hr) | Elster H4000 | ISO4064/BS5728/EEC specification Class B | recommend using K 10:10 | 2 | Yes |
|  |  | 0.13 m3/hr – 160 m3/hr (200 m3/hr) | Elster H5000 | (MID) Directive 2004/22/EC | Integrated communication cable. | 2, or 4 with splitter | Yes |
|  | Combination | 15 l/hr – 60 m3/hr (120 m3/hr) | Elster C4000 | (MID) Directive 2004/22/EC | Main meter - PR7, Low flow meter - PR6 unit | 2 (on each) | Yes |
|  | Electromagnetic | 0.4 m3/hr – 160 m3/hr (200 m3/hr)** | Elster Q4000 | (MID) Directive 2004/22/EC | MX39 dual output Pulser or MX35 dual output remote display | 2 | Yes |
|  |  | 1.0 m3/hr – 160 m3/hr (200 m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 0.79 m3/hr – 250 m3/hr (313 m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |
| 150mm | Woltmann | 4.5 m3/hr – 150 m3/hr (300 m3/hr) | Elster H4000 | ISO4064/BS5728/EEC specification Class B | PR7 unit 100 l/pulse, dual output recommend use K 10:10 | 2 | Yes |
|  |  | 0.13 m3/hr – 160 m3/hr (200 m3/hr) | Elster H5000 | (MID) Directive 2004/22/EC | Integrated communication cable. | 2, or 4 with splitter | Yes |
|  | Combination | 60 l/hr – 150 m3/hr (300 m3/hr) | Elster C4200 | German National Approval | Main meter - PR7, Low flow meter - T-probe | 2 (on each) | Yes |
|  | Electromagnetic | 1 m3/hr – 400 m3/hr (500 m3/hr)** | Elster Q4000 | CEN pr14154, ISO4064, OIML R49 | MX39 dual output Pulser or MX35 dual output remote display | 2 | Yes |
|  |  | 2.5 m3/hr – 400 m3/hr (500 m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 2.0 m3/hr – 630 m3/hr (788 m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |

| 200mm | Electromagnetic | 1.6 m3/hr – 630 m3/hr (788 m3/hr)** | Elster Q4000 | (MID) Directive 2004/22/EC | MX39 dual output Pulser or MX35 dual output remote display | 2 | Yes |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 3.9 m3/hr – 630 m3/hr (788 m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 3.2 m3/hr – 1000m3/hr (1250m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |
| 250mm | Electromagnetic | 6.8m3/hr – 1000m3/hr (1250 m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 5.1 m3/hr – 1600m3/hr (2000m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |
|  |  | 2.5 m3/hr – 1000m3/hr (1250 m3/hr)** | Elster Q4000B Flanged | JIS B8570 conforms to (MID) Directive 2004/22/EC | MX39 dual output Pulser or MX35 dual output remote display | 2 | Yes |
| 300mm | Electromagnetic | 10 m3/hr – 1600 m3/hr (2000m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 7.9 m3/hr – 2500m3/hr (3125m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |
|  |  | 2.5 m3/hr – 1000m3/hr (1250 m3/hr)** | Elster Q4000B Flanged | JIS B8570 conforms to (MID) Directive 2004/22/EC | MX39 dual output Pulser or MX35 dual output remote display | 2 | Yes |
| 350mm | Electromagnetic | 25 m3/hr – 1600 m3/hr (2000m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 12.7m3/hr – 4000m3/hr (5000m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |
| 400mm | Electromagnetic | 40 m3/hr – 2500 m3/hr (3125m3/hr) | ABB AquaMaster | OIML R49 | Variable output determined by user | 1 | Yes |
|  |  | 12.7m3/hr – 4000m3/hr (5000m3/hr) | ABB WaterMaster | OIML R49, (MID) 2004/22/EC | Pulsed output & 4-20mA signal available | 2 | Yes |

Pulse Unit Data

# Pulse Unit Information

| Make | Size | Model | Year | Pulse Enabled | Pulse Type | Pulse switch | Pulse rates Output 1 | Pulse rates Output 2 | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sappel | 15mm | Altair | up to 2010 | Yes* | Magnetic | Sappel Pulsar V3 (Hall) | 1 | N/A | Please note that some internal Sappel meters may already be AMR From 2012 ALL Sappel meters will be AMR |
| Sappel | 15mm | Altair | 2010 - present | Yes** | Magnetic & Inductive | Sappel Pulsar V3 (Hall) or Sappel RCi 3.5 (Ind) | 1 | N/A | Please note that some internal Sappel meters may already be AMR From 2012 ALL Sappel meters will be AMR |
| Sappel | 20mm | Altair | up to 2010 | Yes* | Magnetic | Sappel Pulsar V3 (Hall) | 1 | N/A | Please note that some internal Sappel meters may already be AMR From 2012 ALL Sappel meters will be AMR |
| Sappel | 20mm | Altair | 2010 - present | Yes** | Magnetic & Inductive | Sappel Pulsar V3 (Hall) or Sappel RCi 3.5 (Ind) | 1 | N/A | Please note that some internal Sappel meters may already be AMR From 2012 ALL Sappel meters will be AMR |
| Elster/Kent | 15 & 20mm | V210/V200 | up to 2006 | Yes | Magnetic | MSN pulse unit | 1 | N/A |  |
| Elster/Kent | 15 & 20mm | V210/V200 | 2006 - present | Yes | Inductive | PR6 | 1 | 1 |  |
| Elster/Kent | 15 & 20mm | PSM | up to 1997 | No | N/A | N/A | N/A | N/A | Recommend exchanging meter - NB new meter will be a Sappel AMR |
| Elster/Kent | 15 & 20mm | PSMT | 1997 - present | Yes | Magnetic | T-Probe | 0.5 | N/A |  |
| Elster/Kent | 15 & 20mm | V100 |  | Yes | Magnetic | T-Probe | 0.5 | N/A |  |
| Elster/Kent | 25mm | V210/V200 | up to 2006 | Yes | Magnetic | MSN pulse unit | 1 | N/A |  |
| Elster/Kent | 25mm | V210/V200 | 2006 - present | Yes | Inductive | PR6 | 1 | 1 |  |
| Elster/Kent | 25mm | PSM | up to 1997 | No | N/A | N/A | N/A | N/A | Recommend exchanging meter |
| Elster/Kent | 25mm | PSMT | from 1997 | Yes | Magnetic | T-Probe | 5 | N/A |  |
| Elster/Kent | 25mm | V100 |  | Yes | Magnetic | T-Probe | 5 | N/A |  |
| Elster/Kent | 40mm | PSM | up to 1997 | No | N/A | N/A | N/A | N/A | Recommend exchanging meter |
| Elster/Kent | 40mm | PSMT | from 1997 | Yes | Magnetic | T-Probe | 5 | N/A |  |
| Elster/Kent | 40mm | V100 |  | Yes | Magnetic | T-Probe | 5 | N/A |  |
| Elster/Kent | 50mm | Master |  | Yes | Magnetic | LRP | 1 | N/A |  |
| Elster/Kent | 50mm | H3000 |  | Yes | Magnetic | LRP | 10 | N/A |  |
| Elster/Kent | 50mm | S2000 |  | Yes | Magnetic | Reed switch | 10 | 1000 |  |
| Elster/Kent | 50mm | S2000 | 2010 - present | Yes | Inductive | PR7 | 10 | 10 |  |
| Elster/Kent | 50mm | H4000 |  | Yes | Magnetic | Reed switch | 10 | 1000 |  |
| Elster/Kent | 50mm | H4000 | 2010 - present | Yes | Inductive | PR7 | 10 | 10 |  |
| Elster/Kent | 50mm | H5000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 10 | 10 |  |
| Elster/Kent | 50mm | Q4000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 10 | 1000 |  |
| Elster/Kent | 80mm | Master |  | Yes | Magnetic | LRP | 10 | N/A |  |
| Elster/Kent | 80mm | H3000 |  | Yes | Magnetic | LRP | 10 | N/A |  |
| Elster/Kent | 80mm | S2000 |  | Yes | Magnetic | Reed switch | 10 | 1000 |  |
| Elster/Kent | 80mm | S2000 | 2010 - present | Yes | Inductive | PR7 | 10 | 10 |  |
| Elster/Kent | 80mm | H4000 |  | Yes | Magnetic | Reed switch | 10 | 1000 |  |
| Elster/Kent | 80mm | H4000 | 2010 - present | Yes | Inductive | PR7 | 10 | 10 |  |
| Elster/Kent | 80mm | H5000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 10 | 10 |  |
| Elster/Kent | 80mm | Q4000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 10 | 10 |  |
| Elster/Kent | 100mm | Master |  | Yes | Magnetic | LRP | 10 | N/A |  |
| Elster/Kent | 100mm | H3000 |  | Yes | Magnetic | LRP | 10 | N/A |  |
| Elster/Kent | 100mm | S2000 |  | Yes | Magnetic | Reed switch | 10 | 1000 |  |
| Elster/Kent | 100mm | S2000 | 2010 - present | Yes | Inductive | PR7 | 10 | 10 |  |
| Elster/Kent | 100mm | H4000 |  | Yes | Magnetic | Reed switch | 10 | 1000 |  |
| Elster/Kent | 100mm | H4000 | 2010 - present | Yes | Inductive | PR7 | 10 | 10 |  |
| Elster/Kent | 100mm | H5000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 10 | 10 |  |
| Elster/Kent | 100mm | Q4000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 10 | 10 |  |
| Elster/Kent | 150mm | H3000 |  | Yes | Magnetic | LRP | 100 | N/A |  |
| Elster/Kent | 150mm | H4000 |  | Yes | Magnetic | Reed switch | 100 | 10000 |  |
| Elster/Kent | 150mm | H4000 | 2010 - present | Yes | Inductive | PR7 | 100 | 100 |  |
| Elster/Kent | 150mm | H5000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 100 | 100 |  |
| Elster/Kent | 150mm | Q4000 |  | Yes | inbuilt | Built in - Meter has a 'flying lead' | 100 | 100 |  |
| Schlumberger | 15mm | Aquadis P40/P40M |  | Yes | Inductive | Cyble Sensor | 1 | N/A | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 20mm | Aquadis |  | Yes | Inductive | Cyble Sensor | 1 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 25mm | Aquadis |  | Yes | Inductive | Cyble Sensor | 1 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 40mm | Aquadis |  | Yes | Inductive | Cyble Sensor | 1 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 40mm | Flowstar M |  | Yes | Inductive | Cyble Sensor | 1 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 50mm | Flowstar M |  | Yes | Inductive | Cyble Sensor | 10 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 50mm | Woltex |  | Yes | Inductive | Cyble Sensor | 10 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 80mm | Flowstar M |  | Yes | Inductive | Cyble Sensor | 10 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 80mm | Woltex |  | Yes | Inductive | Cyble Sensor | 10 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 100mm | Flowstar M |  | Yes | Inductive | Cyble Sensor | 10 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 100mm | Woltex |  | Yes | Inductive | Cyble Sensor | 10 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 150mm | Woltex |  | Yes | Inductive | Cyble Sensor | 100 |  | Requires extra care during installation and identifying pulse rates |
| Schlumberger | 200mm | Woltex |  | Yes | Inductive | Cyble Sensor | 100 |  | Requires extra care during installation and identifying pulse rates |
| ABB | All Sizes | AquaMaster |  | Yes | **** | Contact meter services for additional information | **** | **** |  |
| ABB | All Sizes | MagMaster |  | Yes | **** | Contact meter services for additional information | **** | **** |  |
| ABB | All Sizes | WaterMaster |  | Yes | **** | Contact meter services for additional information | **** | **** |  |
| Socam | 15mm | 501 L |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange - NB new 15mm meter will be an AMR |
| Socam | 15mm | 510 PR |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange - NB new 15mm meter will be an AMR |
| Socam | 20mm | 501 L |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange - NB new 20mm meter will be an AMR |
| Socam | 20mm | 510 PR |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange - NB new 20mm meter will be an AMR |
| Socam | 25mm | 501 L |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 25mm | 510 PR |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 40mm | 510 PR |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 50mm | WP |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 50mm | WS |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 80mm | WP |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 80mm | WS |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 100mm | WP |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 100mm | WS |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 150mm | WP |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |
| Socam | 150mm | WS |  | See Comments | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Not recommended for data logging | Pulse units can be difficult to source any reliability is an issue. Recommend meter exchange |

# Elster Bulk Meter Product selector